## Sheet1
Annex B - Financial Offer Form
RFP/UNHCR/JOR/2022/09
FOR THE ESTABLISHMENT OF A FRAME AGREEMENT FOR THE PROVISION OF MAINTENANCE, OPERATION, MONITORING AND CLEANING FOR SOLAR PLANTS IN AZRAQ REFUGEE CAMP
Company Name
Currency |  | JOD
This offer shall be as per the below given scenario and VAT exempt
This offer shall be all-inclusive (i.e. to include logistics and any activity necessary to carry out the tasks/installation stated in the ToR and/or of items)
SN | Item | Description | Specification | Unit | Unit price | Installation cost | Quantity/year | Total price (JOD)
1 | Cleaning | Dry Cleaning Phase 1 (2 MW) | Soft cloth or mop. Non-abrasive only. Not prohibited to use Bristle brush, sponge, squeegee | no. |  |  | 24
2 |  | Dry Cleaning Phase 2 (1.5 MW) | Soft cloth or mop. Non-abrasive only. Not prohibited to use Bristle brush, sponge, squeegee | no. |  |  | 24
3 |  | Dry Cleaning Phase 3 (1.5 MW) | Soft cloth or mop. Non-abrasive only. Not prohibited to use Bristle brush, sponge, squeegee | no. |  |  | 24
|  | Wet Cleaning Phase 1 (2 MW) | Cleaning shall be done between dusk and dawn. Water and power provided by contractor - Hard water prohibited - water shall be free from oil, other liquids, debris, excessive turbidity, odors, total hardness <75 mg/L, calcium 75 mg/L max - Max water pressure at nozzle 35bar - Detergent use subject to approval on case by case basis | no. |  |  | 6
|  | Wet Cleaning Phase 2 (1.5 MW) | Cleaning shall be done between dusk and dawn. Water and power provided by contractor - Hard water prohibited - water shall be free from oil, other liquids, debris, excessive turbidity, odors, total hardness <75 mg/L, calcium 75 mg/L max - Max water pressure at nozzle 35bar - Detergent use subject to approval on case by case basis | no. |  |  | 6
|  | Wet Cleaning Phase 3 (1.5 MW) | Cleaning shall be done between dusk and dawn. Water and power provided by contractor - Hard water prohibited - water shall be free from oil, other liquids, debris, excessive turbidity, odors, total hardness <75 mg/L, calcium 75 mg/L max - Max water pressure at nozzle 35bar - Detergent use subject to approval on case by case basis | no. |  |  | 6
| Inspection | Daily inspection and submission of filled daily inspection check-list | Twice per business day, submission of inspection check-list within 24 hours | no. |  |  | 522
|  | Weekly Inspection and submission of report | Once per week, submission of inspection report maximum by first day of next business week | no. |  |  | 52
| Monitoring and Reporting | Submission of monthly report for all phases | Includes PV performance, maintenance, measurements and tests | no. |  |  | 12
|  | Submission of annual report for all phases | Includes PV performance | no. |  |  | 1
| Performance of Tests | Transformers: Tan Delta, Winding resistance, Short Circuit Impedance (Capacity Test) | Per plant | no. |  |  | 1
|  | MV cable: very low frequency test | Per plant | no. |  |  | 1
|  | Polarity Test | Per plant | no. |  |  | 1
|  | Voltage Test | Per plant | no. |  |  | 1
|  | All PV string tests | per plant Earth, continuity, arc fault… etc. | no. |  |  | 3
|  | MCCB test | Test as needed for mechanical, thermal, magnetic functions, insulation resistance | no. |  |  | 6
|  | Insulation Resistance Test | per plant | no. |  |  | 1
|  | Continuity Test | per plant | no. |  |  | 1
|  | Earthing Test | per plant | no. |  |  | 1
| Security | Security in loco per phase | 24/7, every day of the year including holidays | days |  |  | 365
|  | Remote monitoring/security service through CCTV systems | Fee per day/24hours | days |  |  | 365
| Emergency Visit | Emergency Visit to reach UNHCR projects | Within 2 hours from call. This is applicable when requested by UNHCR Engineer outside working hours | no. |  |  | Upon request
| Spare Parts (all-inclusive; repair/replace/fees/labor/transportation… etc.) | PV solar panels 265 W | 265 W no mismatching permitted with existing - IEC61215, IEC61730, TuV Certified POLY Crystalline Module 5 busbar solar cell Higher module conversion Efficiency 17.26% or higher Half cell ISO9001, ISO14001, OHSAS18001 | pcs |  |  | 60
|  | PV solar panels 275 W | 275 W no mismatching permitted with existing - IEC61215, IEC61730, TuV Certified POLY Crystalline Module 5 busbar solar cell Higher module conversion Efficiency 17.26% or higher Half cell ISO9001, ISO14001, OHSAS18001 | pcs |  |  | 40
|  | PV solar panels 285 W | 285 W - no mismatching permitted with existing - IEC61215, IEC61730, TuV Certified POLY Crystalline Module 5 busbar solar cell Higher module conversion Efficiency 17.26% or higher Half cell ISO9001, ISO14001, OHSAS18001 | pcs |  |  | 40
|  | Three Phase Inverter | Efficiency 98.8% or higher Highest PV system availability with 60kW units DC input voltage of up to 1000V flexible DC solutions with PV array junction boxes I / AC:III; DC: II IEC62109-1/IEC62109-2 (Class I, grounded - communication Class II, PELV), UL1741-w.non-isolated EPS interactive PV inverters, IEEE1547 VERITAS Approved Suitable with existing system as per site visit - origin and technical specs same quality or higher | pcs |  |  | 20
|  | DC Combiner Box | switching device comination is a string combiner box for up to 12 or 14 PV strings UK10.3HESI1000V fuse modular terminal blocks The positive pole of the solar strings is connected to the UK10,3-HESI 1000V fuse modular terminal blocks The negative pole of the solar strings is connected to the STU35/4X10 BU feed-through terminal blocks or as well to UK10,3-HESI 1000V fuse modular terminal blocks The output cables are connected to the UKH150 and UKH150BU high current terminal blocks or to the load break switch. IP65 Polycarbonate housing Connection of up to 12 or 14 solar strings | pcs |  |  | 20
|  | MCCB 400A | 400A - 3 pole AC DC 6kv utilisation category A 36kA breaking capacity at 400-415V IEC/ EN 60947 UL 508 H 50 kA 415 V AC durability 10000 cycle mech, 5000 cycle electrical, backplate mounting, ip20 IEC 60529 or higher, ik07 IEC 62262 or higher, -25 to 70 C operating temperature 18 months warranty or more | pcs |  |  | 10
|  | MCCB 160A | 3 pole AC DC 6kv utilisation category A 50kA breaking capacity at 400-415V IEC/ EN 60947 UL 508 H 50 kA 415 V AC durability 10000 cycle mech, 3000 cycle electrical, backplate mounting, ip20 IEC 60529 or higher, ik07 IEC 62262 or higher, -25 to 70 C operating temperature 18 months warranty or more | pcs |  |  | 10
|  | MCCB 125A | 3 pole AC DC 6kv utilisation category A 36kA breaking capacity at 400-415V IEC/ EN 60947 UL 508 H 50 kA 415 V AC durability 10000 cycle mech, 5000 cycle electrical, backplate mounting, ip20 IEC 60529 or higher, ik07 IEC 62262 or higher, -25 to 70 C operating temperature 18 months warranty or more | pcs |  |  | 20
|  | 160-400A Adjustable breaker | 3 pole AC 8kv utilisation category A 50kA at 380-480V IEC/ EN 60947 UL 508 N AC durability 15000 cycle mech, 6000 cycle electrical, backplate mounting, ip40 IEC 60529 or higher, ik07 IEC 62262 or higher, -25 to 70 C operating temperature 18 months warranty or more | pcs |  |  | 10
|  | Busbar 20/10 | 20/10mm, Pure copper, Insulated with heat shrink 1000V, operating temperature -55C-135C degrees, UL, CSA, MIL, color for each phase including all needed link bends/curves and accessories i.e. nuts, bolts, heat shrink… etc. | m |  |  | 50
|  | Busbar 30/10 | 30/10mm, Pure copper, Insulated with heat shrink 1000V, operating temperature -55C-135C degrees, UL, CSA, MIL, color for each phase including all needed link bends/curves and accessories i.e. nuts, bolts, heat shrink… etc. | m |  |  | 50
|  | Busbar 20/5 | 20/5mm, Pure copper, Insulated with heat shrink 1000V, operating temperature -55C-135C degrees, UL, CSA, MIL, color for each phase including all needed link bends/curves and accessories i.e. nuts, bolts, heat shrink… etc.
|  | Busbar 30/5 | 30/5mm, Pure copper, Insulated with heat shrink 1000V, operating temperature -55C-135C degrees, UL, CSA, MIL, color for each phase including all needed link bends/curves and accessories i.e. nuts, bolts, heat shrink… etc.
|  | Combiner Box fuses | PV / 1000VDC - 15A - cartridge type | pcs |  |  | 15
|  | Modular Surge Arrester | Type 1 + 2, 230/400V AC 3p 350V remote signalling single contacts !SD (1 C/O) Electrical Distribution Network Type, IT230 TN-C earthing systems, Imax 50kA, Iimp 12.5kA, <1.5 kV type 1 max voltage protection, clip-on mounting, DIN rail support, response time <=25ms EN61643-11:2012, IEC 61643-11:2011, CE, IP40 front, IP20 built-in IEC 60529, -25-60C operating temperature | pcs |  |  | 5
|  | Distribution board | Wall mounted - IP65 - 600mm*400mm*200mm | pcs |  |  | 5
|  | Weather Station | Class 2 thermopile pyranometer ISO 9060:1990, adjustable solar irradiance sensor for global or plane of array, PV panel back temperature sensor, ambient air sensor, modbus RTU communication, stainless steel hardware, 2 year warranty, optional add-on sensors, wide operating temperature range, weather resistant, SunSpec certified - US, EU, UK or Japanese origin | pcs |  |  | 1
|  | Monitoring Screen | LED A++ or A+++ 32" | pcs | Example: 10% |  | 1 |  | (=Cost+Profit percentage)
|  | HD-TVI Analog Camera | IP Bullet camera, 2.8 to 12mm motorized lens IR range up to 40m 720p Dual power IP66 Suitable with existing system as per site visit - Same quality or higher | pcs |  |  | 10
|  | DVR | HD-TVI Hybrid 8/16 Channel recorder up to 4/8 IP cameras real-time recording 48 Terabyte Suitable with existing system as per site visit - Same quality or higher | pcs |  |  | 1
|  | NVR | 16/32/64 channel h.265 NVR 2U real-time recording 48terabyte Suitable with existing system as per site visit - Same quality or higher | pcs |  |  | 1
|  | Power Supply | Universal 12VDC 3.5A Suitable with existing system as per site visit - Same quality or higher | pcs |  |  | 2
|  | 6mm DC Cables | Temperature range -40 °C to +90 °C, Max. temp. at conductor +120 °C, tin plated copper, Nominal voltage According to VDE U0 /U 600/1000 V AC // 1800 V DC conductor/conductor - double insulated - Ozone resistant acc. to EN 50396 - Weather and UV resistant HD 605/A1 - Halogen-free EN 50267-2-1, EN 60684-2 Resistant to acid and bases EN 60811-2-1 Flame-resistant VDE 0482-332-1-2 DIN EN 60332-1-2, IEC 60332-1 Abrasion-resistant sheath DIN EN 5351 Resistant to short-circuits up to 200°C, short-circuits temperature 200°C/ 5 sec, service life - 25 years, Hydrolysis and ammoniac resistant, TuV certified | m |  |  | 500
|  | 4mm DC Cables | Temperature range -40 °C to +90 °C, Max. temp. at conductor +120 °C, tin plated copper, Nominal voltage According to VDE U0 /U 600/1000 V AC // 1800 V DC conductor/conductor - double insulated - Ozone resistant acc. to EN 50396 - Weather and UV resistant HD 605/A1 - Halogen-free EN 50267-2-1, EN 60684-2 Resistant to acid and bases EN 60811-2-1 Flame-resistant VDE 0482-332-1-2 DIN EN 60332-1-2, IEC 60332-1 Abrasion-resistant sheath DIN EN 5351 Resistant to short-circuits up to 200°C, short-circuits temperature 200°C/ 5 sec, service life - 25 years, Hydrolysis and ammoniac resistant, TuV certified | m |  |  | 600
|  | Aluminum Cables | 1*300sqmm Armoured OVC insulated cables 600/1000V according to BS6346 and IEC60502-1 Annealed Copper or Aluminum Conductor according to IEC 60228 Insulation PVC type TI 1 according to BS6346 or Type PVC/A according to IEC60502-1 Bedding extruded black PVC Armor Aluminum wires for single core Sheating: PVC tpe TM 1 according to BS6346 or Type ST1 according to IEC 60502-1 | m |  |  | 300
|  | Aluminum Cables | 1*240sqmm Armoured OVC insulated cables 600/1000V according to BS6346 and IEC60502-1 Annealed Copper or Aluminum Conductor according to IEC 60228 Insulation PVC type TI 1 according to BS6346 or Type PVC/A according to IEC60502-1 Bedding extruded black PVC Armor Aluminum wires for single core Sheating: PVC tpe TM 1 according to BS6346 or Type ST1 according to IEC 60502-1 | m |  |  | 300
|  | Copper Rod | Copper purity is 99.95%., Tensile strength over 600N/mm2, Lifetime 28 years, Rod Diameter 17.2MM length 1.2m | pcs |  |  | 5
|  | Flood Lights (Specify spec) | 220-240V, 50Hz, Color temperature 6500K, Luminous flux 17,000 lm or higher, lifetime 30,000 hours or higher, IP65 or IP67, Temperature range -20…+55 °C, 1 year warranty | pcs |  |  | 20
|  | Cable tie 10cm | UV resistant compatible with DC cables above | pcs |  |  | 400
|  | Cable tie 30cm | UV resistant compatible with DC cables above | pcs |  |  | 400
|  | MC4 cables male and female 4sqmm | UV resistant compatible with DC cables above | pcs |  |  | 200
|  | MC4 cables male and female 6sqmm | UV resistant compatible with DC cables above | pcs |  |  | 400
|  | Inverter Manager | Compatible with Inverter specs above Suitable with existing system as per site visit - Same quality or higher | pcs |  |  | 1
|  | Switch for Inverter Manager | Data communications 8 RJ45 port DIN Rail Mount Unmanaged Ethernet Switch, 10Mbit/s, 100Mbit/s Suitable with existing system as per site visit - Same quality or higher | pcs |  |  | 1
|  | Galvanized paint | Volume Solids (ASTM D2697) 46 ± 2% SPECIFIC GRAVITY 1.5 ± 0.05 Theoritical spreading range 11.5 - 9.2 sqm/Ltr Recommended Dry Film Thickness 40 - 50 microns/coat Recommended Wet Film Thickness 88 - 110 microns/coat Flash point 38°C | kg |  |  | 3
|  | Earth cable 1*120sqmm soft drawn | 1*120sqmm soft drawn bare copper conductor max temperature 80°C - max DC resistance per KM at 20°C is 0.153Ohm - BS EN 60228 IEC 60228 | m |  |  | 50
|  | Earth cable 1*50sqmm soft drawn | 1*50sqmm soft drawn bare copper conductor max temperature 80°C - max DC resistance per KM at 20°C is 0.387Ohm - BS EN 60228 IEC 60228 | m |  |  | 50
|  | Earth cable 1*120sqmm plain annealed | 1*120sqmm plain annealed copper stranded conductor with PVC TI3 1.6mm insulation as per IEC 60227 Green and Yellow - Rated 450/750V max temperature 80°C - max DC resistance per KM at 20°C is 0.153Ohm max AC resistance per KM at 20C is 0.1968Ohm - BS EN 60228 IEC 60228 | m |  |  | 50
|  | 3*4sqmm cable | CU/XLPE/SWA/PVC | m |  |  | 300
|  | 2*2.5sqmm cable | CU/XLPE/SWA/PVC | m |  |  | 300
|  | 4*50sqmm cable | CU/XLPE/SWA/PVC | m |  |  | 300
|  | 1*150sqmm cable | CU/XLPE/SWA/PVC | m |  |  | 300
|  | 1*120sqmm cable | Earthing CU/PVC | m |  |  | 300
|  | 1*70sqmm cable | Earthing CU/PVC | m |  |  | 300
|  | 1*50sqmm cable | Flexible cable CU/PVC | m |  |  | 300
|  | Data Cable | Cat6a Solid UTP Acc. to ISO/IEC11801 EN50173 EIA/TIA568-A CATERGORY 7 Flame retardant IEC60332-1-2 Smoke density IEC61034 Suitable with existing system as per site visit - Same quality or higher | m |  |  | 300
|  | Fiber Optic Cable | 4 Core 9/125 Suitable with existing system as per site visit - Same quality or higher | m |  |  | 300
|  | PVC Pipes 50 Inch | UV resistant | m |  |  | 200
|  | PVC Pipes 32 Inch | UV resistant | m |  |  | 200
|  | PVC Pipes 25 Inch | UV resistant | m |  |  | 500
|  | PVC Pipes 20 Inch | UV resistant | m |  |  | 500
|  | Cable trunk 50*100mm | PVC Electric | m |  |  | 50
|  | Cable trunk 20*10mm | PVC Electric | m |  |  | 50
|  | Enclosures | Polyester Reinforced with Fiberglass IP65 With Canopy Height 1000mm - Width 750mm - Depth 320mm Tin plated Copper Busbars 30x5mm 3Phase and Earth
|  | 2.5m steel pole | galvanized steel including concrete base | pcs |  |  | 5
|  | 3m steel pole | galvanized steel including concrete base | pcs |  |  | 5
|  | Switchgear or any related internal component | 36 kV, 2500A, (1000V breaker insulation) 25kA 1s-3s, peak 65kA/ 70/80 kV insulation, IP3X, Vacuum Circuit Breaker, -25 - 40°C, IEC62271-200 , IAC class) / IEEE Std C37.20.7 (1D-S class), IEC 62271-200, IEC 62271-102, IEC61243-5, IEC62271-1, IEC62271-200, IEC62271-103, IEC62271-102, IEC62271-100, IEEE C37.74, IEEE C37.20.3, IEEE 1247, IEEE C37.123, IEEE Std C37.20.4, IEEE C37.04, IEEE C37.06, IEEE Std C37.09, IEEE C37.20.7 For internal components shall be of same or higher quality as existing | pcs | Example: 10% |  | 1 |  | (=Cost+Profit percentage)
|  | 1500 KVA transformer or any related component inside | Step up 415V/33kV ISO9001:2000 Complied with IEC 60076, IEC 60354, IDECO, EDCO, JEPCO Working Temp up to 45 Hermetically sealed Tapping ±2.5% - ±5% Dyn11 Frequncy 50Hz Oil immersed type, same quality or higher than the exisiting based on site visit | pcs | Example: 10% |  | 1 |  | (=Cost+Profit percentage)
|  | MV Cables | 1*150sqmm 19/33(36) kV single-core Aluminum Class 2 XLPE Insulated, copper wire screen, hard drawn aluminum wire armor, PVC sheathe cable black to IEC60502-2:2005, IEC 60332-1, | m |  |  | 85
|  | MV Cables | 1*240sqmm 19/33(36) kV single-core Aluminum Class 2 XLPE Insulated, copper wire screen, hard drawn aluminum wire armor, PVC sheathe cable black to IEC60502-2:2005, IEC 60332-1, | m |  |  | 10
|  | First Aid Kit | containing: Up to date first-aid manual list of emergency phone numbers Sterile gauze pads of different sizes adhesive med tape adhesive bandages (band-aids) in several sizes Elastic bandage Splint Antiseptic wipes Splint soap Antibiotic ointment antiseptic solution (like hydrogen peroxide) Hydrocortisone cream (1%) acetaminophen and ibuprofen tweezers sharp scissors safety pins disposable instant cold packs calamine lotion alcohol wipes or ethyl alcohol mouthpiece for giving CPR plastic non-latex gloves (at least 2 pairs) | pcs |  |  | 3
|  | Fence | Galvanized 2.7 meters high cross link fence consisting of 5.5cm*5.5cm*3.65mm with a 2 inch diameter and 2.8mm thickness and 3.5 total high steel pipes every 2 meters, 3 meters above the ground. 80cm steel angle 40*40*4mm bended forward at angle 45 degrees for the outside fense with 3 line of barbed wire to be fixed on top. 1 line of razor wire 1 meter diameter to be fixed between the fence. Supplying and installing a main 5x10 cm high bridge 3 meter total height supported with two steel pipes 2 inch diameter and 2.8 mm thickness for each H bridge for corners. Supply and install 4 lines horizontal wires 2.9mm diameter fixing, fittings and 50*50*50 cm minimum square concerete bases for the supports. Price must include constructed a tie foundation of 20 cm depth (10 cm above ground and 10cm underground)*15cm width al aong the fence (outside and inside) including all civil works, wood works, excavation and restoring the original surface. if the length of the fence exceeds 25 meters, two diagonal pipes have to be provided and installed to supprt the middle (for every 25m) all bracing pipes to be welded). Concrete foundation Spec 50cm*50cm*50cm hole filled with concrete mix with stones. Providing and casting a normal conrete (cement: fine aggregate: coarse aggregate ratio of 1:3:6) with minimum breaking load of 15MPA after 28 days, concrete curing at least of 3 day periods and all to complete the job, supply and install welded steel bar 40 cm length, 8mm diameter at the bottom of galvanized pipe 20cm | m |  |  | 100
|  | Double Swing Gate | 5m width, 2m height - Delivery and installation within` 24 hours including holdays Supply materials, equipment and labor for manufacturing if needed, a swing vehicle gate. Covering material is galvanized chain link fence consisting of 5.5cm*5.5cm*3.65mm. Price must include installing three 8cm strong heavy duty welded with H bridge (5*10cm), welding overlap between dor frame and h-bridge 16mm). A rubber wheel shall be installed for each part. Provide and install two crossing pipes for each side of the gate. Price must include installing concrete fottings 50*50*50 cm with steel support and two downward sliding locks of 12mm diameter | pcs |  |  | 1
|  | Double Swing Gate | 6m width, 2.5m height - Delivery and installation within 24 hours including holdays Supply materials, equipment and labor for manufacturing if needed, a swing vehicle gate. Covering material is galvanized chain link fence consisting of 5.5cm*5.5cm*3.65mm. Price must include installing three 8cm strong heavy duty welded with H bridge (5*10cm), welding overlap between dor frame and h-bridge 16mm). A rubber wheel shall be installed for each part. Provide and install two crossing pipes for each side of the gate. Price must include installing concrete fottings 50*50*50 cm with steel support and two downward sliding locks of 12mm diameter | pcs |  |  | 1
|  | Battery | 12V 18Ah | pcs |  |  | 9
|  | Charger | 600W, 122Vdc, 230Vac (187-264Vac) | pcs |  |  | 2
|  | Air Conditioner split unit | 18,000 BTU - DC inverter technology - Ductless - 220-240V SEER / EER 20/12.5 HSPF / COP 10/3.35 | pcs |  |  | 1
|  | Fire Alarm Sensor | ceiling mounted, AA battery powered | pcs |  |  | 3
|  | Mid clamp | Fix panel to structure - Aluminum/steel must be suitable with existing structure | pcs |  |  | 200
|  | End clamp | Fix panel to structure - Aluminum/steel must be suitable with existing structure | pcs |  |  | 200
|  | Cable lug | 4mm cord end - 99% copper tin electro-plated | pcs |  |  | 200
|  | Cable lug | 6mm cord end - 99% copper tin electro-plated | pcs |  |  | 200
|  | Fire extinguisher maintenance | CO2 | pcs |  |  | 9
|  | Fire extinguisher | CO2 | pcs |  |  | 3
| License | Pay fees and/or renew license | Fully as per EMRC guidelines and provide documents and receipts to UNHCR | no. | Example: 10% |  | 2 |  | (=Cost+Profit percentage)
Location: Azraq
By signing this offer the bidder acknowledges and accepts the UNHCR General Conditions of Contracts for the Provision of Goods and Services (Annex X) and the UN Supplier Code of Conduct (Annex X), and commits to hold their offers' validity for (90) days
N.B : The highlighted in yellow is recommended to be priced as cost on contractor + overhead/profit percentage as these items prices may vary significantly over the course of a FA