## Sheet2
Annex C1 - Financial Offer Form (RFP/UNHCR/JOR/2022/17) - Zaatari Camp
COMPANY NAME:
CURRENCY:
This Offer shall be as per the below given scenario and VAT exempt. The offer shall be all-inclusive (i.e. to include any activity necessary to carry out the tasks stated in the TOR)
SN | Description |  | Specification | Unit | Quantity / year | Unit Price | Installation Cost | TOTAL Price
1 | Preventive | LV Network Regular Checks | Check jumper clips status and replace the broken | activity | 365 |  |  | 0
|  |  | Check clamps status and replace the faulty ones | activity | 365 |  |  | 0
|  |  | Check suspenders status and replace the faulty ones | activity | 365 |  |  | 0
|  |  | Check cable’s sag | activity | 365 |  |  | 0
|  |  | Check poles and correct the slopping poles | activity | 52 |  |  | 0
|  |  | Check poles and treat the rust if it found | activity | 52 |  |  | 0
|  |  | Check stays tension and replace or correct the faulty ones | activity | 52 |  |  | 0
|  |  | Check cable termination and insolation and replace or correct the faulty ones | activity | 365 |  |  | 0
|  |  | Check all streets lighting units at all plots, markets and ring road lighting and replace or correct the faulty ones | activity | 52
|  |  | Balancing the loads of the transformer’s phases | activity | 52
|  | Consumer cables and connections regular checks | Check jumper clips of consumer cables and replace or correct the faulty ones. | activity | 365
|  |  | Check the consumer cables and insulate it with heat shrink if needed / Once a day and replace or correct the faulty ones. | activity | 365
|  |  | Check the consumer cable fixation at the top of pole and shelter and replace or correct the faulty ones | activity | 52
|  |  | Check cable connection at the consumer unit and replace or correct the faulty ones | activity | 52
|  |  | Check cables tension and replace or correct the faulty ones | activity | 12
|  |  | Check earth leakage breaker and MCB breakers status and replace or correct the faulty ones | activity | 12
|  |  | Check consumer internal wiring and connections and correct or replace | activity | 12
|  | Transformers rooms and Main distribution boards (MDB) Regular Checks | Check the main circuit breaker status and replace or correct the faulty ones | activity | 52
|  |  | Check all the LV cables connections from starting from the transformer till the poles | activity | 52
|  |  | Check all second circuits’ breakers status and replace or correct the faulty ones | activity | 52
|  |  | Check automated breakers status and calibration and replace or correct the faulty ones | activity | 52
|  |  | Check timers’ status (battery and work status) and replace or correct the faulty ones | activity | 52
|  |  | Check (photocell, conductor, and three-position switches) status and replace or correct the faulty ones | activity | 52
|  |  | Check Copper cables lugs status inside the MDB (insulation and fixation) and replace or correct the faulty ones | activity | 52
|  |  | Check the control wires connection and status and replace or correct the faulty ones | activity | 52
|  |  | Check the bus-bars insulation and replace or correct the faulty ones | activity | 52
|  |  | Check holes at the bottom of MDB and close it suitably and replace or correct the faulty ones | activity | 52
|  |  | Check doors (locks, paint, hinges, and rubber) and replace or correct the faulty ones | activity | 52
3 | Reporting | Reports | Daily report | pcs | 365 |  |  | 0
|  |  | Weekly report | pcs | 52
|  |  | Monthly report | pcs | 12 |  |  | 0
4 | Corrective | Corrective activities is only upon the request of UNHCR field engineer, and quantity shown is the expected frequency and might subject to change | Dismantling electrical materials from vacant or damaged shelters/Caravans, and store it in the bidder Storage Area | activity | 100 |  |  | 0
|  |  | Storage Area Inventory Count | activity | 12 |  |  | 0
|  |  | New internal wiring for the new vacant shelters/caravans | activity | 200 |  |  | 0
|  |  | Maintain the internal wiring for the damaged shelters/caravans | activity | 200 |  |  | 0
|  |  | Install new cables on LV Poles | m | 1000 |  |  | 0
|  |  | Connecting new caravan/shelters to the grid | activity | 1000 |  |  | 0
|  |  | Installing LV poles | Pole | 200 |  |  | 0
|  |  | Installing MDBs | activity | 20 |  |  | 0
|  |  | Disconnecting vacant caravans/shelters | activity | 1000 |  |  | 0
|  |  | Provide technical assessment and BoQ | activity | 100 |  |  | 0
|  |  | Installing street Lights units | Unit | 200 |  |  | 0
| Testing | MDB testing | Volts: Phase to phase /phase to neutral / phase to earth / earth to neutral for all MDBs in the camp | activity | 12 |  |  | 0
|  |  | Ampere: Measure the load (ampere) on each phase individually | activity | 12 |  |  | 0
|  |  | Earth resistance in the MDB and Measure the earth resistance at earth bus bar | activity | 12 |  |  | 0
|  |  | Continuity Tests for All Stretched Cables | activity | 12 |  |  | 0
|  |  | Insulation Tests for copper cables | activity | 12 |  |  | 0
|  |  | Thermal imaging test for MDBs | activity | 2 |  |  | 0
|  | Consumer Unit Testing Selecting random addresses thorough UNHCR electrical engineer, and make these measurements | Volts:Phase to neutral / phase to earth / neutral to earth. | activity | 52 |  |  | 0
|  |  | Ampere:Measure the load at chosen addresses by UNHCR engineer | activity | 52 |  |  | 0
|  | Earth system Tests | Check the earth resistance in different locations (shelters, poles, MDB and Transformer Room) and conduct necessary actions for corrections | activity | 12 |  |  | 0
|  |  | Check the earth resistance at the main ground point; it should be not more than 5 Ω (ohm) and conduct necessary actions for corrections | activity | 12 |  |  | 0
|  |  | Check the earth connections and replace the broken clips | activity | 12 |  |  | 0
6 | Estimated spare parts | Low Voltage Poles 10m with all accessories | TUV Certified Galvanized 82-120 Micron Yield Strength N/mm2 420-461 Tensile Strength N/mm2 545-570 Elongation % 32-38 | pcs | 30 |  |  | 0
|  | Low Voltage Poles 9m with all accessories | TUV Certified Galvanized 82-120 Micron Yield Strength N/mm2 420-461 Tensile Strength N/mm2 545-570 Elongation % 32-38 | pcs | 30 |  |  | 0
|  | Steel cable stay | With all needed accessories 35 to 50 mm2 galvanized from 55-70 micro | pcs | 80 |  |  | 0
|  | Feeders Poles 12 m with all accessories | TUV Certified Galvanized 82-120 Micron Yield Strength N/mm2 420-461 Tensile Strength N/mm2 545-570 Elongation % 32-38 | pcs | 10 |  |  | 0
|  | Low Voltage pole Concrete Base | According to Jordanian Civil Engineering Standard | pcs | 50 |  |  | 0
|  | LED Fixtures for the Plots Street 60W | 90-260 Input Voltage 100 lm/W TUV Certified Heat Dissipation 4000 – 6000 K CE certified IP 65 50-60Hz | pcs | 100 |  |  | 0
|  | LED Fixtures for the Plots Street 30 W | 90-260 Input Voltage 100 lm/W TUV Certified Heat Dissipation 4000 – 6000 K CE certified IP 65 50-60Hz | pcs | 100 |  |  | 0
|  | LED Fixtures for the Plots Street 90 W | 90-260 Input Voltage 100 lm/W TUV Certified Heat Dissipation 4000 – 6000 K CE certified IP 65 50-60Hz | pcs | 100 |  |  | 0
|  | Cross Arm 2.5m with all needed accessories | Galvanized 45-55 Micron | pcs | 100 |  |  | 0
|  | Insulation plastic ring for lighting | For street lighting | pcs | 150 |  |  | 0
|  | LV 1x 300 mm2 | CU/XLPE/SWA/PVC | m | 300 |  |  | 0
|  | LV 1x 70 mm2 | CU/XLPE/SWA/PVC | m | 100 |  |  | 0
|  | LV 1x 120 mm2 | CU/XLPE/SWA/PVC | m | 300 |  |  | 0
|  | LV 4x95+50mm2 | CU/XLPE/SWA/PVC | m | 100 |  |  | 0
|  | LV 1x 185 mm2 | CU/XLPE/SWA/PVC | m | 100 |  |  | 0
|  | LV 4X35mm2 | CU/XLPE/SWA/PVC | m | 100 |  |  | 0
|  | LV 4x120+70mm2 | CU/XLPE/SWA/PVC | m | 100 |  |  | 0
|  | LV 4x240+120mm2 | CU/XLPE/SWA/PVC | m | 100 |  |  | 0
|  | LV 4x300+150mm2 | CU/XLPE/SWA/PVC | m | 100 |  |  | 0
|  | LV4x400+240mm2 | CU/XLPE/SWA/PVC | m | 100 |  |  | 0
|  | LV 4x185+120mm2 | CU/XLPE/SWA/PVC | m | 300 |  |  | 0
|  | TWISTED 4AL (4X185 mm2) | ALLOY/XLPE | m | 400 |  |  | 0
|  | TWISTED 3AL+AL+AL. (3*150 mm2)+50+95 | ALLOY/XLPE | m | 50 |  |  | 0
|  | TWISTED 3AL+AL+AL. (3*150 mm2)+50+95 | ALLOY/XLPE | m | 100 |  |  | 0
|  | TWISTED 3AL+AL+AL. (3*120 mm2)+35+70 | ALLOY/XLPE | m | 500 |  |  | 0
|  | TWISTED 3AL+AL+AL. (3*95 mm2)+25+50 | ALLOY/XLPE | m | 100 |  |  | 0
|  | TWISTED 3AL+AL+AL. (3*70 mm2)+25+35 | ALLOY/XLPE | m | 500 |  |  | 0
|  | TWISTED 3AL+AL+AL. (3*50 mm2)+16+25 | ALLOY/XLPE | m | 100 |  |  | 0
|  | TWISTED 3AL+AL+AL. (3*35 mm2)+25+25 | ALLOY/XLPE | m | 100 |  |  | 0
|  | TWISTED 3AL+AL+AL. (3*25 mm2)+25+25 | ALLOY/XLPE | m | 100 |  |  | 0
|  | TWISTED 3AL+AL+AL. (3*10 mm2) | ALLOY/XLPE | m | 1000 |  |  | 0
|  | LV 3x4mm2 | CU/XLPE/SWA/PVC | m | 500 |  |  | 0
|  | LV 3x6mm2 | CU/XLPE/SWA/PVC | m | 200 |  |  | 0
|  | LV 3x2.5 mm2 | CU/XLPE/SWA/PVC | m | 200 |  |  | 0
|  | LV 2x2.5 mm2 | CU/XLPE/SWA/PVC | m | 150 |  |  | 0
|  | LV 5x16mm2 2 | CU/XLPE/SWA/PVC | m | 150 |  |  | 0
|  | LV 4x25mm2+1x16mm2 | CU/XLPE/SWA/PVC | m | 150 |  |  | 0
|  | LV 4x50mm2+1x25mm2 | CU/XLPE/SWA/PVC | m | 150 |  |  | 0
|  | TWISTED 3AL+AL+AL. (3*16 mm2)+16+16 | ALLOY/XLPE | m | 100 |  |  | 0
|  | TWISTED 3AL+AL+AL. (3*25 mm2)+25+25 | ALLOY/XLPE | m | 150 |  |  | 0
|  | TWISTED 3AL+AL+AL. (3*50 mm2)+50+50 | ALLOY/XLPE | m | 150 |  |  | 0
|  | 10A MCB |  | pcs | 30 |  |  | 0
|  | 16A MCB |  | pcs | 30 |  |  | 0
|  | RCBO | RCBOs shall be rated for 240Vac, 50Hz with breaking/making capacity of 120A rms, short circuit withstand current lcw of 2kA rms for 1 second, rated short circuit making capacity of 3kA peak and short circuit conditional current of 6A rms MCB’s and RCBO’s shall be rated for 230V/400V; 50Hz, short circuit capacity Ics/Icn of 6,000A | pcs | 300 |  |  | 0
|  | Consumer Unit | Consumer units shall be surface mounted with IP3X-rated insulated housing with DIN rails for mounting of circuit breakers. Each shall be suitable for 230V, 50Hz electrical connections, 16sqmm2 solid-stranded cable terminations and shall have adequate wiring space and cable entry points. Each consumer unit shall contain, 10A MCB for lighting circuits, 16A MCB for socket circuits and shall have adequate space to house 2 No. additional MCB’s. Consumer units shall be wall-mounted inside each shelter at a height of 2metres, close to the door as detailed on the drawings. | pcs | 300 |  |  | 0
|  | 18W LED bulb with Holder | E27 CRI 80 6500 K A+ 25,000 Hours | pcs | 100 |  |  | 0
|  | 15W LED bulb with Holder | E27 CRI 80 6500 K A+ 25,000 Hours | pcs | 100 |  |  | 0
|  | 2 gang PVC switch | 10 Amp 250 V | pcs | 100 |  |  | 0
|  | 1gang PVC switch | 10 Amp 250 V | pcs | 100 |  |  | 0
|  | Earthing Rods | 1 Copper purity is 99.95%. Tensile strength over 600N/mm2 Lifetime 28 years Rod Diameter 17.2mm | pcs | 500 |  |  | 0
|  | MCCB 400A | 3Pole 100KA, adjustable | pcs | 30 |  |  | 0
|  | MCCB 250A | 3Pole 50KA, adjustable | pcs | 30 |  |  | 0
|  | MCCB 200A | 3Pole 50KA, adjustable | pcs | 10 |  |  | 0
|  | MCCB 100 A | 3Pole, adjustable | pcs | 20 |  |  | 0
|  | MCCB 20A | 3Pole 35KA | pcs | 10 |  |  | 0
|  | Contactor | 7.5KW 18A AC.3 | pcs | 30 |  |  | 0
|  | MCCB 160A | 3Pole 36KA, adjustable | pcs | 10 |  |  | 0
|  | MCCB 1000A | 3Pole 100KA, adjustable | pcs | 20 |  |  | 0
|  | MCCB 630A | 3Pole 70KA, adjustable | pcs | 20 |  |  | 0
|  | MCCB 1600A | 3Pole, adjustable | pcs | 15 |  |  | 0
|  | Base for Fuse 630 Ampere | 630 A, 690 V, 50 Hz, IEC60269 | pcs | 50 |  |  | 0
|  | Base for Fuse 400 Ampere | 400 A, 690 V, 50 Hz, IEC60269 | pcs | 50 |  |  | 0
|  | Base for Fuse 250 Ampere | 250 A, 690 V, 50 Hz, IEC60269 | pcs | 50 |  |  | 0
|  | connector isolation piercing | 16-150 mm2 / 16-120 mm2 | pcs | 2000 |  |  | 0
|  | connector isolation piercing | 16-120 mm2 / 16-185 mm2 | pcs | 500 |  |  | 0
|  | connector isolation piercing for lighting | 10 - 95 mm2 / 1.5 - 10 mm2 | pcs | 1000 |  |  | 0
|  | connector isolation piercing for consumers Households | 10 - 95 mm2 / 1.5 - 10 mm2 | pcs | 1000 |  |  | 0
|  | connector isolation piercing for consumers Households | 4- 95 mm2/4 mm-120 mms | pcs | 1000 |  |  | 0
|  | Raintight Photoelectric Control | 208-277 V, 50/60 Hz, capacity = 3000 VA | pcs | 30 |  |  | 0
|  | AC contactors | 110 A, Max fuse= 200A, short circuit= 5kA, NC7-9511, 230 V, 50/60 HZ, IEC/EN 60947-4-1 | pcs | 30 |  |  | 0
|  | Suspension clamps and brackets | 50 to 120 cables | pcs | 200 |  |  | 0
|  | Cable lug | 300 mm2 for Cu cables | pcs | 100 |  |  | 0
|  | Cable lug | 185 mm2 for Cu cables | pcs | 100 |  |  | 0
|  | Cable lug | 120 mm2 for Cu cables | pcs | 100 |  |  | 0
|  | Cable lug | 185 mm2 for AL cables | pcs | 100 |  |  | 0
|  | Cable lug | 120 mm2 for Al cables | pcs | 100 |  |  | 0
|  | Cable lug | 70 mm2 for Al cables | pcs | 100 |  |  | 0
|  | Cable lug | 50 mm2 for Al cables | pcs | 100 |  |  | 0
|  | Cable lug | 35 mm2 for Cu cables | pcs | 100 |  |  | 0
|  | Cable lug | 50 mm2 for Cu cables | pcs | 100 |  |  | 0
|  | Cable lug | 10 mm2 for Al cables | pcs | 100 |  |  | 0
|  | Cable lug | 4 mm2 for Cu cables | pcs | 100 |  |  | 0
|  | Safety boots | Safety isolation, insulated, steel or safety toe, rubber outsold, anti-static | pcs | 15 |  |  | 0
|  | Safety gloves | Safety isolation of electrical direct and indirect, voltage | pcs | 15 |  |  | 0
|  | Safety belts | for electrical poles | pcs | 4 |  |  | 0
|  | Safety helmets | With light for electricians. | pcs | 15 |  |  | 0
|  | Hydraulic lug crimping machine | Cables range between 35mm2 till 300 mm2 | pcs | 2 |  |  | 0
|  | Vest for electricians | Antifire, water resistant | pcs | 20 |  |  | 0
|  | Voltage Detectors stick | • designed for checking transmission lines, power distribution equipment, down power lines, fuses, and load break connectors | pcs | 1 |  |  | 0
|  | surface-mounted double-socket | TUV Certified 16A 230V IP42-rated 2P+E With Shutters | pcs | 20 |  |  | 0
|  | surface-mounted Single-socket | TUV Certified 16A 230V IP42-rated 2P+E With Shutters | pcs | 30 |  |  | 0
|  | MDB Distribution boards and switchgear necessary for the protection of cabling and equipment within the complete electrical installation in accordance with IEC 62271 and IP67-rated. This shall include for all necessary supports, steelworks, concrete etc. to properly complete the installation of these boards and connecting cabling. Main distribution board shall be installed at each transformer location. These shall be IP65-rated with key-lockable doors including all necessary supports, structures, glands etc. All distribution boards shall be designed with 20% additional space capacity for future installation of extra MCCB’s. | within the complete electrical installation in accordance with IEC 62271 and IP67-rated. This shall include for all necessary supports, steelworks, concrete etc. to properly complete the installation of these boards and connecting cabling A main distribution board shall be installed at each transformer location. These shall be IP65-rated with key-lockable doors including all necessary supports, structures, glands etc. All distribution boards shall be designed with 20% additional space capacity for future installation of extra MCCB’s. A separate MCCB shall be installed for each separate cable supplying electrical power to any building or area | pcs | 4 |  |  | 0
|  | Motor operator for MCCB'S | For MCCB 630 A 3 poles, 4X630A Front motor operator Plate for mounting and interlocking | pcs | 10 |  |  | 0
|  | 630 Amp Fuse | Fuse Standard DIN 43620-1, DIN 43620-3, IEC 60269, VDE 0636 Voltage Rating 500 V ac 120 KA SC | pcs | 10 |  |  | 0
|  | 500 Amp Fuse | Fuse Standard DIN 43620-1, DIN 43620-3, IEC 60269, VDE 0636 Voltage Rating 500 V ac 120 KA SC | pcs | 10 |  |  | 0
|  | 315 Amp Fuse | Fuse Standard DIN 43620-1, DIN 43620-3, IEC 60269, VDE 0636 Voltage Rating 500 V ac 120 KA SC | pcs | 10 |  |  | 0
|  | 250 Amp Fuse | Fuse Standard DIN 43620-1, DIN 43620-3, IEC 60269, VDE 0636 Voltage Rating 690 V ac 65 KA SC | pcs | 10 |  |  | 0
|  | 200 Amp Fuse | Fuse Standard DIN 43620-1, DIN 43620-3, IEC 60269, VDE 0636 Voltage Rating 690 V ac 65 KA SC | pcs | 10 |  |  | 0
|  | 160 Amp Fuse | Fuse Standard DIN 43620-1, DIN 43620-3, IEC 60269, VDE 0636 Voltage Rating 690 V ac 65 KA SC | pcs | 10 |  |  | 0
|  | CABLE 1C X 185 MM2 | CU/XLPE/PVC | m | 200 |  |  | 0
|  | CABLE 1C X 300 MM2 | CU/XLPE/PVC | m | 300 |  |  | 0
|  | CABLE 4C X 185 MM2 | CU/XLPE/PVC | m | 200 |  |  | 0
|  | Bolt with nut | 12 cm, 10 mm2 | pcs | 1000 |  |  | 0
|  | Clement | For 10 mm2 AL cables or 4 mm2 Cu cables | pcs | 1000 |  |  | 0
|  | Bolt self-drill | 10 cm | pcs | 1000 |  |  | 0
|  | Plank wood | 2.5 LM, 5cm * 10 cm | pcs | 300 |  |  | 0
|  | Self-drill screws | 3 cm | pcs | 1000 |  |  | 0
|  | Steel cables stay wielding |  | pcs | 200 |  |  | 0
|  | Main MDB Busbar | Compatible case by case related to the MDB connections With all needed accessories | pcs | 10 |  |  | 0
|  | MCCB 630 A iron base with accessories |  | pcs | 10 |  |  | 0
|  | Main Busbar for 250A MCCB |  | m | 10 |  |  | 0
|  | Main Busbar for 1000 A MCCB |  | m | 10 |  |  | 0
|  | Main Busbar for 400A MCCB |  | m | 10 |  |  | 0
|  | Main Busbar for 1600A MCCB |  | m | 10 |  |  | 0
|  | Main Busbar for 630 MCCB |  | m | 10 |  |  | 0
|  | Cable entry busbar 630A with accessories |  | m | 10 |  |  | 0
|  | Cable entry busbar 1000 A with accessories |  | m | 10 |  |  | 0
|  | Cable entry busbar 1600 A with accessories |  | m | 10 |  |  | 0
|  | Cable entry busbar 250 A with accessories |  | m | 10 |  |  | 0
|  | Cable entry busbar 400 A with accessories |  | m | 10 |  |  | 0
|  | Pole Dismantling, welding, and extension |  | pcs | 50 |  |  | 0
|  | Earth pit |  | pcs | 20 |  |  | 0
|  | Rod to clamp junction |  | pcs | 20 |  |  | 0
|  | U Bolt Earth Rod Clamp |  | pcs | 30 |  |  | 0
|  | Coupler | For 120 mm2 cables | pcs | 50 |  |  | 0
|  | Coupler | 185 mm2 cables | pcs | 50 |  |  | 0
|  | Coupler | 300 mm2 cables | pcs | 50 |  |  | 0
|  | Cable Gland 120 mm |  | pcs | 50 |  |  | 0
|  | Cable Gland 150 mm |  | pcs | 50 |  |  | 0
|  | Bentonite (Kg) |  | kg | 15 |  |  | 0
|  | Circuit breaker Bolts | MCCB 630 | pcs | 30 |  |  | 0
|  | Circuit breaker Bolts | MCCB 250 | pcs | 30 |  |  | 0
|  | Circuit breaker Bolts | MCCB 1000 | pcs | 30 |  |  | 0
|  | Circuit breaker Bolts | MCCB 1600 | pcs | 30 |  |  | 0
|  | Circuit breaker Bolts | MCCB 400 | pcs | 30 |  |  | 0
|  | PVC Pipe 20mm2 with accessories | 3 meters | pcs | 50 |  |  | 0
|  | Pole clamps | 10 meters poles | pcs | 100 |  |  | 0
|  | Pole clamps | 9 meters poles | pcs | 100 |  |  | 0
|  | Pole clamps | Form MV poles | pcs | 50 |  |  | 0
|  | clamp PVC Pipe | 20 mm | pcs | 50 |  |  | 0
|  | Tensions cable clamp | 3*10 mm2 AL cable | pcs | 100 |  |  | 0
|  | Tensions cable clamp | 3*4 mm2 Cu cable | pcs | 100 |  |  | 0
|  | Rubber clamp for cables fixation | 3*10 mm2 AL cable | pcs | 100 |  |  | 0
|  | Rubber clamp for cables fixation | 3*4 mm2 Cu cable | pcs | 100 |  |  | 0
|  | Heat shrinks | For 185 mm2 cables, Red/blue/green | m | 400 |  |  | 0
|  | Heat shrinks | For 120 mm2 cables, Red/blue/green | m | 200 |  |  | 0
|  | Dead end clamp |  | pcs | 100 |  |  | 0
|  | Distribution board | Included all accessories, CB 10A * Qty 5, Isolator 2P 63A IP 65 waterproof | pcs | 10 |  |  | 0
|  | Tensions cable clamp | For 120 mm2 AL cable | pcs | 100 |  |  | 0
|  | Cable tie | For 120 mm2 + 10 mm2 cables | pcs | 200 |  |  | 0
|  | Suspender |  | pcs | 100 |  |  | 0
|  | End cap (Plastic) | For Network cables (185mm2 +120 mm) | pcs | 100 |  |  | 0
|  | End Cable Clamp |  | pcs | 100 |  |  | 0
|  | End pole cap (ring) line end | 9 meters poles | pcs | 50 |  |  | 0
|  | Current transformer | MCCB 1600 | pcs | 20 |  |  | 0
|  | Current transformer | MCCB 1000 | pcs | 20 |  |  | 0
|  | Bolt with nut | 6 mm | pcs | 1000 |  |  | 0
|  | Current transformer | MCCB 630 | pcs | 20 |  |  | 0
|  | Cable joint | 185 mm2 cable AL, 120 mm2 Cable AL | pcs | 100 |  |  | 0
|  | Room master locks | Master large locks | pcs | 30 |  |  | 0
|  | Electrical tape | Standard, high quality | pcs | 100 |  |  | 0
|  | Isolation tape for electrical cables | High quality | pcs | 100 |  |  | 0
|  | 24-hour timer | 12 – 24 V UC, 50 – 60 Hz, DIN rail, 96 switching segments, Switching capacity at 250 V AC, 16A, Manual switch with 3 positions: Continuous ON/AUTO/continuous OFF | pcs | 10 |  |  | 0
|  | Timer battery | Compatible with existing timers | pcs | 10 |  |  | 0
TOTAL |  |  |  |  | 0
By signing this offer the bidder acknowledges and accepts the UNHCR General Conditions of Contracts for the Provision of Goods and Services (Annex X) and the UN Supplier Code of Conduct (Annex F), and commits to hold their offer's validity for ninety (90) days