## ESTIMATE
UNHCR PAKISTAN
SOLARIZATION OF THQ HOSPITAL CHAKDARA UNDER RAHA PROGRAMME - 2022
600 KW ON GRID SOLAR SYSTEM
ENGINEER'S ESTIMATE
ITEM No. | KP MRS 2022 REF. No./NS | DESCRIPTION | UNIT |  | QTY | UNIT RATE (PKR.) | TOTAL AMOUNT (PKR.)
(a) | (b) | (c) | (d) |  | (e) | (f) | (g)
SOLAR SYSTEM (PHOTOVOLTAIC)
A. |  | SCHEDULED ITEMS
1 | 26-01-d-01 | Supply and Erection of Solar PV Module (Solar Panel) Mono-crystalline A-Grade (per Watt) (As per Approved Specifications) Mono Perk Half cut | 1 | Watt | 600000
2 | 26-01-m-01 | Supply and Erection of hot dipped (80 microns Average) galvanized steel of minimum thickness of 12 SWG / 2.64 mm Channel / Pipe or 8 SWG / 4.06 mm Angle | 1 | Watt | 600000
3 | 26-01-i-03-d | Supply and Erection of GRID TIE INVERTER (ON-Grid Inverter) | 1 | Per Watt | 600000
4 | 26-01-g-03 | Supply and Erection 1x6 sq.mm single core (XPLE/XPLO insulated/PCV sheathed) flexible copper cable | 1 | Rft | 22000 |  |  |  | 15000
5 | 26-01-g-04 | Supply and Erection 1x10sq.mm Copper cable (G/Y Flexible) | 1 | Rft | 3000
6 | 26-01-g-06 | Supply and Erection 1x25sq.mm Copper cable (G/Y Flexible) | 1 | Rft | 1000
7 | 26-01-b-01 | Supply and Erection PVC flexible pipe : 1" i/d | 1 | Rft | 1800
8 | 15-02-a-03 | Supply and Erection PVC pipe for wiring purpose complete On surface including clamps etc.: 1" i/d | 1 | Rft | 2000
9 | 26-01-n-03 | Supply and Erection of Stainless Steel Nuts and Bolts | 1 | Watt | 600000
10 | 26-01-h-01 | Supply and Erection MC4 connector (TUV Approved) | 1 | Pair | 100
11 | 26-01-h-02 | Supply and Erection MC4 Branch connector | 1 | Pair | 50
12 | 15-105-a | Supply & erection of Earth Rod | 1 | Each | 30
B. |  | LT CABLES/CABLE TRAY, CONDUITS & PIPES
Supply at site, installation, testing and commissioning of PVC insulated un-armoured copper conductor cable 600 / 1000 Volt grade (or otherwise mentioned in cable description ) in prelaid conduits / trenches to be installed as per routes shown on drawings including cost of all necessary materials, connections, identification tags, cables lugs properly crimped at both ends for the following sizes complete in all respects
13 | 15-122-g | 70 sq mm , 4 core PVC/PVC stranded copper conductor cable | 1 | RMtr | 80
14 | 15-122-j | 185 sq mm , 4 core PVC/PVC stranded copper conductor cable MDB Solar Panel to Existing LT Panel Busbar and From Existing LT Panel to Transformer (Optional) | 1 | RMtr | 50
15 | 15-135-e | Supply at site, fabrication and installation of GI perforated cable tray 14 SWG 8 ft. to 10 ft. long with sides 3" high to be installed on wall, or in vertical, or above false ceiling in horizontal position or floor mounted or as shown on drawing, including cost of hanging arrangement brackets made of angle iron 38mm x 38mm x 6mm installed at every 3 ft., cost of all necessary fixing accessories, complete in all respects.(100mm*75mm) | 1 | Rft | 3000
16 | 15-135-b | Supply at site, fabrication and installation of GI perforated cable tray 14 SWG 8 ft. to 10 ft. long with sides 3" high to be installed on wall, or in vertical, or above false ceiling in horizontal position or floor mounted or as shown on drawing, including cost of hanging arrangement brackets made of angle iron 38mm x 38mm x 6mm installed at every 3 ft., cost of all necessary fixing accessories, complete in all respects.(300mm*100mm) | 1 | Rft. | 800
17 | 24-18-C-08 | Providing, laying, cutting, jointing, testing and disinfecting UPVC pressure pipeline in trenches (conforming to BS 3505 manufactured ) jointed with socket, elbow, tee, bend and plug bend etc. Manufactured by the respective manufacturer complete as per specifications uPVC Pressure Pipes Class D (12 Bar) except excavation. 6" Nominal Pipe Size (NPS) | 1 | Rft | 600
18 | 06-05-f | Plain Cement Concrete including placing, compacting, finishing & curing (Ratio 1:2:4) | 100 | Cft | 150
19 | 06-05-f | Plain Cement Concrete including placing, compacting, finishing & curing (Ratio 1:2:4) (1'x1'x1') Foundation for Solar Panels Structure) | 100 | Cft | 450
Cost of Scheduled Items: PKR.
Add 8% above on Scheduled Item for District lower dir (chakdara) (Rs.)
Total Cost of Scheduled Items (Rs.)
C. |  | NON-SCHEDULED ITEMS
(Ref. Spec. 8001 , 8133, 8212, 8240, 8290)
20 | NS-01 | Providing and fixing Lightning Arrestor 1" Copper rod 6ft long with 4'' Bowl five spikes complete in all respect (above top structure level) | 1 | No. | 10
21 | NS-02 | Providing and fixing Earth Connecting Point 12"x1.5"x 6-8mm insulators with complete Accessories. | 1 | No | 10
22 | NS-03 | Providing and fixing of 75mmx10mm copper Busbar in addition with Existing LT Panel Busbar RYB | 1 | RFT | 60
23 | NS-04 | MAIN DISTRIBUTION BOX
LT Panel shall be made from 14 SWG sheet steel, while all other DBs must be of 14SWG. This shall be designed, fabricated and manufactured as a free standing floor type or Wall Mounted. The sheet metal work shall be cleaned down to bare shining metal degreased, derusted and painted with TWO base coats of antirust RED paint. The sheet metal work shall be finished in TWO coats of powder paint. The color and shade shall be as approved by the Engineer. The distribution Board shall be complete with all internal wirings, tags, identification labels, TPN and E copper busbars, accessories etc. The DB should be provided with the armored glands. The bus-bars shall be insulated in RED, YELLOW, BLUE and BLACK insulations. The insulation shall be heat shrinkable type or as directed by the Engineer.
Includes
1 No MCCB 400A 4 POLE 50KA
6 No MCCB 200A 4 POLE 35KA
05 No Volt meter Digital
05 No Amp meter Digital
01 No Energy Analayser
03*5 Nos. R-Y,B Indication lamps. control fuses
Bus Bar RYB N E
5 no o/u voltage and OL Protection Phase failure
1 No Interphase protection relay
5 No SPD
|  | Includes other Necessary Equipment as per Instruction as per single Line diagram or as required to complete the necessary Requirement | 1 | Job | 3
GREEN ENERGY METER & CONTROL EQUIPMENT
24 | NS-05 | Supply and Erection of Green Meter including Certification Regulations or Related NEPRA and PESCO Fee for installation and Activation of Green Energy Meter include Grid Flow Study from approved consultant of PESCO | 1 | Job | 1
25 | NS-06 | Providing Fixing and Configuration of Gen Set Controller with all Mounting and Control Accessories | 1 | Job | 1
26 | NS-07 | Providing Fixing of water Proof Type DC Distribution box MCB/FUSES for Each Strings (for each Inverter) including DC Breakers SPD with Terminals Complete in all respects | 1 | Job | 6
27 | NS-08 | Providing and Fixing of Weather station includes Wind Speed humidity,Ambbient temperature module Temperature control cable complete in all respect | 1 | Job | 1
28 | NS-09 | Providing and Fixing of Monitoring and Communication OEM Logger (4G Dongle) | 1 | Job | 6
29 | NS-10 | Providing and Fixing of 1.5 ton Split AC in Invertor room including Copper Piping control Cables and Power Wiring complete in all respect | 1 | Job | 3
30 | NS-11 | EARTHING
|  | Earth Electrode for earthing of DBs shall comprise of 75mm x 4877 mm x 6 mm thick copper plate With 4 Nos. 6 mm dia brass nuts ,bults and washers 70 sqmm HDHC copper wire as earthing leads. A 100 mm dia Medium Duty GI pipe shall be used with 10 mm dia holes @500 mm c-c. The total length of this GI pipe should be 45 ft. A 150 mm dia 60 ft long hole should be drilled in ground by percussion method and above mentioned 100 mm dia medium duty GI pipe should be fixed in this hole simultaneously up to the depth of 45 ft from NSL. | 1 | Job | 3
Cost of Non-Scheduled Items: PKR.
Total Cost of Scheduled & Non-Scheduled Items: PKR.
Note: Payment of all Items will be paid as per actual execution on site
RECOMMENDATION
545 W Each Solar Panels
03 No. 200 KW Systems
0