## Summary
UNHCR PAKISTAN
SOLARIZATION OF THQ HOSPITAL THALL UNDER RAHA PROGRAMME-2022
Summary of Engineers Estimates
S.No | Name | Cost (PKR) | Description of Works
A. | Hopital Buildings | 0 | 70 KW Off Grid Hybrid Solar System
B. | Tube Well | 0 | 20 KW On Grid Solar System
Total Cost (Rs.) |  | 0

## THALL
UNHCR PAKISTAN
SOLARIZATION OF THQ HOSPITAL THALL UNDER RAHA PROGRAMME - 2022
70 KW OFF GRID HYBRID & 20 KW ON GRID SOLAR SYSTEM
ENGINEER'S ESTIMATE
ITEM No. | KP MRS 2022 REF. No./NS | DESCRIPTION | UNIT |  | QTY | UNIT RATE (PKR.) | TOTAL AMOUNT (PKR.)
(a) | (b) | (c) | (d) |  | (e) | (f) | (g)
A. |  | 70 KW OFF GRID HYBRID SOLAR SYSTEM HOSPITAL BUILDINGS
SCHEDULED ITEMS
A1. |  | LT CABLES CONDUITS & PIPES
1 | 15-02-a-02 | Supply and Erection PVC pipe for wiring purpose complete On surface including clamps etc: 3/4" i/d | 1 | Rft | 1500
2 | 15-79-d | PVC conduit for surface wiring (duraduct) 2" including all charges for nail screws etc | 1 | Rft. | 400
3 | 15-02-a-03 | Supply and Erection PVC pipe for wiring purpose complete On surface including clamps etc: 1" i/d | 1 | Rft | 600
A2. |  | SOLAR SYSTEM (PHOTOVOLTAIC)
4 | 26-01-d-01 | Supply and Erection of Solar PV Module (Solar Panel) Mono-crystalline A-Grade (per Watt) (As per Approved Specifications) | 1 | Watt | 70000
5 | 26-01-m-01 | Supply and Erection of hot dipped (80 microns Average) galvanized steel of minimum thickness of 12 SWG / 2.64 mm Channel / Pipe or 8 SWG / 4.06 mm Angle | 1 | Watt | 70000
6 | 26-01-i-05 | Supply and Erection off Grid Hybrid inverter with Dual MPPT charge Controler | 1 | Per Watt | 70000
7 | 26-01-f-06 | Supply and Erection of 12 V Lithium LiFeP04 battery per KWhr | 1 | KWhr | 105
8 | 26-01-o | Supply and Erection of BOX / STAND for Batteries SHS Inverter & Charge Controller | 1 | Watt | 70000
9 | 26-01-g-03 | Supply and Erection 1x6 sq.mm single core (XPLE/XPLO insulated/PCV sheathed) flexible copper cable | 1 | Rft. | 12000
10 | 26-01-g-04 | Supply and Erection 1x10sq.mm Copper cable (G/Y Flexible) | 1 | Rft | 1200
11 | 26-01-g-06 | Supply and Erection 1x25sq.mm Copper cable (Flexible) | 1 | Rft | 400
12 | 15-122-b | 10sq mm , 4 core PVC/PVC stranded copper conductor cable | 1 | RMtr | 300
13 | 26-01-n-02 | Supply and Erection of 1x1 ft 4mm Copper Earthing Plate | 1 | Watt | 70000
14 | 6-01-n-03 | Supply and Erection of Stainless Steel Nuts and Bolts | 1 | Watt | 70000
15 | 26-01-h-01 | Supply and Erection MC4 connector (TUV Approved) | 1 | Pair | 24
16 | 26-01-h-02 | Supply and Erection MC4 Branch connector | 1 | Pair | 28
17 | 15-105-a | Supply & erection of Earth Rod | 1 | Each | 12
18 | 15-135-e | Supply at site, fabrication and installation of GI perforated cable tray 14 SWG 8 ft. to 10 ft. long with sides 3" high to be installed on wall, or in vertical, or above false ceiling in horizontal position or floor mounted or as shown on drawing, including cost of hanging arrangement brackets made of angle iron 38mm x 38mm x 6mm installed at every 3 ft., cost of all necessary fixing accessories, complete in all respects.(100mm*75mm) | 1 | Rft | 200
19 | 06-05-f | Plain Cement Concrete including placing, compacting, finishing & curing (Ratio 1:2:4) (1'x1'x1') Foundation for Solar Panels Structure) | 100 | Cft | 120
20 | 14-160-b | Electric water coolers of 40 gallons capacity,including inlet and outlet connections, gate valve on inlet, electric onnection upto power socket,and all other accessories for complete installation. | 1 | Each | 5
21 | 14-161 | Triple water filter (10") including inlet and outlet connections, power supply, and all accessories for complete installation. | 1 | Each | 5
Cost of Scheduled Items: PKR. | [7 empty] | 0
Add 5% above on Scheduled Item for District Hangu (Rs.)
Total Cost of Scheduled Items (Rs.)
A3. |  | NON-SCHEDULED ITEMS
22 | NS-01 | Providing and fixing Lightning Arrestor 1" Copper rod 6ft long with 4'' Bowl five spikes complete in all respect (above top structure level) | 1 | No. | 6
23 | NS-02 | Providing and fixing Earth Connecting Point 8"x1.5"x 6-8mm insulators with complete Accessories. | 1 | No | 6
24 | NS-03 | SOLAR CONTROL PANEL
Control Panel includes
1 No Change Over Switch
3 No indication Light
01 No Digital Voltmeter
03 Nos. R- Indication lamps
01 Nos. Earth Bus Bar
01 Nos. Neutral Bus Bar
1 No DC MCCB CHINTor ABB (for Battries)
3 no 63A MCB DC TP for PV STRINGS CHINTor ABB
3 no 40A MCB TP for Load CHINTor ABB
2 Nos. 60A Amps TP MCCB For AC Supply CHINTor ABB
1 no o/u voltage and OL Protection
2 No SPD (DC AND AC)
|  | Includes other Necessary Equioment as per Instruction as per Single Line Diagram | 1 | No | 6
25 | NS-04 | Providing and Fixing of 1.5ton Split AC in Invertor room including Copper Piping controll Cables and Power Wiring complete in All Respect (invertor Room) | 1 | Job | 6
Cost of Non-Scheduled Items: PKR. | [6 empty] | 0
Total Cost of Scheduled & Non-Scheduled Items: PKR. | [6 empty] | 0
RECOMMENDATION EACH BUILDING
| 1 | OT |  | 10 | KW
| 2 | OPD |  | 10 | KW
| 3 | ADMIN |  | 15 | KW
| 4 | EMERGENCY |  | 10 | KW
| 5 | BLOOD BANK DENTAL |  | 10 | KW
| 6 | LAB VACCINE CENTRE AND WARDS |  | 15 | KW
B. |  | 20 KW ON GRID SOLAR SYTEM FOR TUBE WELL
SCHEDULED ITEMS
B1. |  | SOLAR SYSTEM (PHOTOVOLTAIC)
1 | 26-01-d-01 | Supply and Erection of Solar PV Module (Solar Panel) Mono-crystalline A-Grade (per Watt) (As per Approved Specifications) Mono Perk Half cut | 1 | Watt | 20000
2 | 26-01-m-01 | Supply and Erection of hot dipped (80 microns Average) galvanized steel of minimum thickness of 12 SWG / 2.64 mm Channel / Pipe or 8 SWG / 4.06 mm Angle | 1 | Watt | 20000
3 | 26-01-i-03-d | Supply and Erection of GRID TIE INVERTER (ON-Grid Inverter) | 1 | Per Watt | 20000
4 | 26-01-g-03 | Supply and Erection 1x6 sq.mm single core (XPLE/XPLO insulated/PCV sheathed) flexible copper cable | 1 | Rft | 2000
5 | 26-01-g-04 | Supply and Erection 1x10sq.mm Copper cable (G/Y Flexible) | 1 | Rft | 350
6 | 26-01-g-06 | Supply and Erection 1x25sq.mm Copper cable (G/Y Flexible) | 1 | Rft | 200
7 | 26-01-b-01 | Supply and Erection PVC flexible pipe : 1" i/d | 1 | Rft | 300
8 | 15-02-a-03 | Supply and Erection PVC pipe for wiring purpose complete On surface including clamps etc: 1" i/d | 1 | Rft | 400
9 | 26-01-n-03 | Supply and Erection of Stainless Steel Nuts and Bolts | 1 | Watt | 20000
10 | 26-01-h-01 | Supply and Erection MC4 connector (TUV Approved) | 1 | Pair | 15
11 | 26-01-h-02 | Supply and Erection MC4 Branch connector | 1 | Pair | 10
12 | 15-105-a | Supply & erection of Earth Rod | 1 | Each | 4
B2. |  | LT CABLES/CABLE TRAY CONDUITS & PIPES
Supply at site, installation, testing and commissioning of PVC insulated un-armoured copper conductor cable 600 / 1000 Volt grade (or otherwise mentioned in cable description ) in prelaid conduits / trenches to be installed as per routes shown on drawings including cost of all necessary materials, connections, identification tags, cables lugs properly crimped at both ends for the following sizes complete in all respects
13 | 15-122-D | 25sq mm , 4 core PVC/PVC stranded copper conductor cable | 1 | RMtr | 50
14 | 15-135-e | Supply at site, fabrication and installation of GI perforated cable tray 14 SWG 8 ft. to 10 ft. long with sides 3" high to be installed on wall, or in vertical, or above false ceiling in horizontal position or floor mounted or as shown on drawing, including cost of hanging arrangement brackets made of angle iron 38mm x 38mm x 6mm installed at every 3 ft., cost of all necessary fixing accessories, complete in all respects.(100mm*75mm) | 1 | Rft | 200
15 | 03, 051 | Excavation of trench in all kinds of soils except cutting in rock for pilelines upto 1.5m depth | 1000 | Cft | 300
16 | 06-05-f | Plain Cement Concrete including placing, compacting, finishing & curing (Ratio 1:2:4) (1'x1'x1') Foundation for Solar Panels Structure) | 100 | Cft | 20
Cost of Scheduled Items: PKR. | [6 empty] | 0
Add 5% above on Scheduled Item for District Hangu (Rs.) | [6 empty] | 0
Total Cost of Scheduled Items (Rs.) | [6 empty] | 0
B3. |  | NON-SCHEDULED ITEMS
(Ref. Spec. 8001 , 8133, 8212, 8240, 8290)
17 | NS-01 | Providing and fixing Lightning Arrestor 1" Copper rod 6ft long with 4'' Bowl five spikes complete in all respect (above top structure level) | 1 | No. | 1
18 | NS-02 | Providing and fixing Earth Connecting Point 12"x1.5"x 6-8mm insulators with complete Accessories. | 1 | No | 1
19 | NS-03 | MAIN DISTRIBUTION BOX
MDB shall be made from 14 SWG sheet steel, while all other DBs must be of 14SWG. This shall be designed, fabricated and manufactured as a free standing floor type or Wall Mounted. The sheet metal work shall be cleaned down to bare shining metal degreased, derusted and painted with TWO base coats of antirust RED paint. The sheet metal work shall be finished in TWO coats of powder paint. The color and shade shall be as approved by the Engineer. The distribution Board shall be complete with all internal wirings, tags, identification labels, TPN and E copper busbars, accessories etc. The DB should be provided with the armored glands. The bus-bars shall be insulated in RED, YELLOW, BLUE and BLACK insulations. The insulation shall be heat shrinkable type or as directed by the Engineer.
Includes
1 No MCCB 80A 4 POLE 50KA
01 No Volt meter Digital
01 No Amp meter Digital
01 No Energy Analayser
3 Nos. R-Y,B Indication lamps. control fuses
Bus Bar RYB N E
1 no o/u voltage and OL Protection Phase failure
1 No Interphase protection realy
2 No SPD
|  | Includes other Necessary Equipment as per Instruction as per single Line diagram or as required to complete the necessary Requirement | 1 | Job | 1
GREEN ENERGY METER & CONTROL EQUIPMENT
20 | NS-04 | Supply and Erection of Green Meter including Certification Regulations or Related NEPRA and PESCO Fee for installation and Activation of Green Energy Meter | 1 | Job | 1
21 | NS-05 | Providing Fixing of water Proof Type DC Distribution Box MCB/FUSES for Each Strings (for each Inverter) including DC Breakers SPD with Terminals Complete in all respects | 1 | Job | 1
22 | NS-06 | Providing and Fixing of Weather station includes Wind Speed humidity,Ambbient temperature module Temperature control cable complete in all respect | 1 | Job | 1
23 | NS-07 | 100A Change Over Switch (Solar Wapda and OFF) for Tube Well | 1 | Job | 1
24 | NS-08 | Providing and Fixing of Monitoring and Communication OEM Loger (4G Dongel) | 1 | Job | 1
25 | NS-09 | Providing and Fixing of 1.5ton Split AC in Invertor room including Copper Piping controll Cables and Power Wiring complete in All Respect (invertor Room) | 1 | Job | 1
26 | NS-10 | EARTHING
|  | Earth Electrode for earthing of DBs shall comprise of 75mm x 4877 mm x 6 mm thick copper plate With 4 Nos. 6 mm dia brass nuts ,bults and washers 70 sqmm HDHC copper wire as earthing leads.A 100 mm dia Medium Duty GI pipe shall be used with 10 mm dia holes @500 mm c-c. The total length of this GI pipe should be 45 ft. A 150 mm dia 60 ft long hole should be drilled in ground by percussion method and above mentioned 100 mm dia medium duty GI pipe should be fixed in this hole simultaneously up to the depth of 45 ft from NSL. | 1 | Job | 1
Cost of Non-Scheduled Items: PKR.
Total Cost of Scheduled & Non-Scheduled Items: PKR.
Note:Payment of All Items will be paid as per actual execuated at site
RECOMMENDATION
1 No 20kw on Grid Inverter
545 W Each Solar Panels
1 No MDB