## Summary
UNHCR PAKISTAN
CONSTRUCTION OF CCU BLOCK AT DISTRICT HEADQUARTER HOSPITAL, BANNU
SUMMARY
ENGINEER'S ESTIMATE
S.No | DESCRIPTION | TOTAL AMOUNT (Rs.)
1 | Civil Works | 0
2 | Electrical Works | 0
3 | Plumbing Works | 0
4 | Medical Gas Piping Works | 0
Total (A to D) (Rs.) = |  | 0

## 1. Civil
UNHCR PAKISTAN
CONSTRUCTION OF CCU BLOCK AT DISTRICT HEADQUARTER HOSPITAL, BANNU
ENGINEER'S ESTIMATE
CIVIL WORKS
ITEM NO. | KPK MRS 2022 REF. NO. / NS (2nd BI ANNUAL) | DESCRIPTION | UNIT | QTY | UNIT RATE (Rs.) | TOTAL AMOUNT (Rs.)
(a) | (b) | (c) | (d) | (e) | (f) | (g)
SCHEDULED ITEMS
A1. |  | BUILDING CIVIL WORKS
EARTHWORK (EXCAVATION AND EMBANKMENT)
1 | 03-07-b | Earth fill in lawns including dressing & compaction with suitable earth borrowed. | 1000 Cft | 1740 | 0 | 0
2 | 03-18-a | Filling, watering and ramming earth under floor with surplus earth from foundation, etc | 1000 Cft | 25950 | 0 | 0
3 | 03-18-d | Filling, watering and ramming earth under floor with earth excavated from outside lead upto 30m | 1000 Cft | 5500 | 0 | 0
4 | 03-19-a | Extra for every 15 m extra lead or part thereof for earthwork soft, ordinary, hard & very hard upto 250m, 17 Trips, 169.32 x No of Trips. | 1000 Cft | 18480 | 0 | 0
5 | 03-20-a | Transportation of earth all types beyond 250 m and upto 500 m. | 1000 Cft | 18480 | 0 | 0
6 | 03-20-b | Transportation of earth all types for every 100m extra lead beyond 500m upto 1.5 km. 10 Trips, 1095.6 x No. of Trips. | 1000 Cft | 18480 | 0 | 0
7 | 03-20-c | Transportation of earth all types for every 500m extra lead beyond 1.5k upto 8.0 km, 13 Trips, 996 x No. of Trips. | 1000 Cft | 18480 | 0 | 0
8 | 03-25-b | Excavation in foundation of building, bridges etc complete: in ordinary soil. | 1000 Cft | 55670 | 0 | 0
CONCRETE
9 | 06-02 | Dry rammed shingle brick ballast or stone ballast 1.5" to 2" gauge | 100 Cft. | 4030 | 0 | 0
10 | 06-05-h | Plain Cement Concrete including placing, compacting, finishing & curing (Ratio 1:3:6) upto 20' height | 100 Cft. | 770 | 0 | 0
11 | 06-05-h + 06-16-b | Plain Cement Concrete including placing, compacting, finishing & curing (Ratio 1:3:6) upto 20' -30' height | 100 Cft. | 2420 | 0 | 0
12 | 06-05-h + 2x06-16-b | Plain Cement Concrete including placing, compacting, finishing & curing (Ratio 1:3:6) upto 30' -40' height | 100 Cft. | 300 | 0 | 0
13 | 06-05-i | Plain Cement Concrete including placing, compacting, finishing & curing (Ratio 1:4:8) | 100 Cft. | 7245 | 0 | 0
14 | 06-07-a-03 | RCC in roof slab, beam, column & other structural members, insitu or precast. (1:2:4) on reception,nursing counter & vanity | 100 Cft. | 100 | 0 | 0
15 | 06-07-a-03 +06-07-e | 2nd storey. | 100 Cft. | 60 | 0 | 0
16 | 06-08-b | Supply & fabricate M.S. reinforcement for cement concrete (Hot rolled deformed bars Grade 60) | 100 Kg | 157400 | 0 | 0
17 | 06-08-c | Supply & fabricate M.S. reinforcement for cement concrete (Hot rolled deformed bars Grade 40) | 100 Kg | 61327 | 0 | 0
18 | 06-23- | Fill expansion joints with bitumen, sand & saw dust in Ratio 1:2:2 | Rft | 435 | 0 | 0
19 | 6-47-a | Erection and removal of Form work with Steel Surface Finshing for RCC or Plain Concrete in any shape - Position / Horizontal | 100 Sft. | 26230 | 0 | 0
20 | 6-47-b | Erection and removal of Form work with Steel Surface Finshing for RCC or Plain cement Concrete in any shape - Position / Vertical | 100 Sft. | 55520 | 0 | 0
21 | 06-48-a | Class A1 concrete in reinforcement/non reinforcement concrete structure with minimum cylinder compressive strength 3000 psi on 28 days other than concrete in water and piles with consistency range in slump 25-75 mm with water cement ratio 0.58 | 100 Cft. | 37515 | 0 | 0
22 | 06-48-a +06-07-e | 2nd storey. | 100 Cft. | 11880 | 0 | 0
23 | 06-48-a +2x06-07-e | 3rd storey. | 100 Cft. | 2315 | 0 | 0
BRICK MASONRY
24 | 07-04-a-04 | 1st class brick work in foundation and plinth in Cement, sand mortar 1:5 | 100 Cft. | 910 | 0 | 0
25 | 07-05-a-04 | 1st class brick work in ground floor Cement, sand mortar 1:5 | 100 Cft. | 8690 | 0 | 0
26 | 07-05-a-04 + 07-06-a | 1st class brick work in first floor in Cement, sand mortar 1:5 | 100 Cft. | 9030 | 0 | 0
27 | 07-05-a-04 + 07-06-b | 1st class brick work in 2nd floor in Cement, sand mortar 1:5 | 100 Cft. | 1560 | 0 | 0
Roof Treatment
28 | 09-11-a | Earth filling over roof including watering, ramming etc 3" thick earth filling and 1" mud plaster | 100 Sft. | 10160 | 0 | 0
29 | 09-16 | Khuras on roof 2'x2'x6" | Each | 14 | 0 | 0
30 | 09-46 | Providing and Laying Prestressed Roof of Slab/Girder, 2" thick PCC 1:2:4 with chicken mesh, polythene, mud, tar | Sft | 1510 | 0 | 0
FLOORING
31 | 10-03-a | Provide, lay, water & ram clean coarse sand under floor / brick paving, complete. | 100 Sft. | 459.54 | 0 | 0
32 | 10-12 + 10-18 | Brick tiles (9"x4.5"x1.5") laid flat in 1:3 c/s mortar over a bed of 3/4" thick cement mortar 1:6 | 100 Sft. | 10160 | 0 | 0
33 | 10-14-b | Cement concrete tiles laid in 1:2 c/s mortar over 3/4" thick bed of c/s mortar 1:2: 12" x 12" x 1" | 100 Sft. | 1370 | 0 | 0
34 | 10-15-d | Provide & lay topping of concrete 1:2:4, including surface finishing & dividing in panels : 2" thick | 100 Sft. | 870 | 0 | 0
35 | 10-15-d + 10-18 | First floor | 100 Sft. | 2650 | 0 | 0
36 | 10-26-c-i | Provide & lay marble fine dressed stone flooring on surface in white cement complete: 3/4" thick 12" x 12" Super Sunny White Marble | 100 Sft. | 450 | 0 | 0
37 | 10-26-e | Providing and laying marble fine dressed stone 4-5 feet and 12" wide 1" thick for stairs steps. | 100 Sft. | 830 | 0 | 0
38 | 10-37 | Providing and Fixing of Marble Vanity for Wash Hand Basin of Imported approved quality. | 100 Sft. | 40 | 0 | 0
39 | 10-38-a | Providing and Laying 1" Thick Super White marble Slab Exceeding 12"x12" size Kitchen Top in White Cement including all labour for Grinding and Polishing.(nurse room) | Sft. | 80 | 0 | 0
40 | 10-44 | Providing and laying 1/2" thick marble in dado / skirting with matching colour mortar in joints set over 1/2" thick rough cast 1:4 cement sand plaster | 100 Sft. | 1240 | 0 | 0
41 | 10-48 | Providing and Fixing Vinyl Tiles or Vinyl Sheet flooring over firm foundation | 100 Sft. | 2770 | 0 | 0
42 | 10-55-i | Providing and Fixing of Porcelain Floor Tile 12" x 12" of approved quality | 100 Sft. | 1380 | 0 | 0
43 | 10-55-j | Providing and Fixing of Bath Room Tiles 12"x18" of approved quality. | 100 Sft. | 8700 | 0 | 0
44 | 10-58-c | Providing and Fixing of porcelain full body tiles 20" × 20" × 3/8 of approved colour of shade, joint using spacers in white cement with pigment laid on base of CM 1:2 etc complete in all respects. | 100 Sft. | 28090 | 0 | 0
45 | 10-60-a | Providing and laying 3/4"(19mm) thick Granite Black polished tiles of approved quality of any size on floor over 3/8" thick base cement sand mortar 1:3 including setting the tiles with portland cement slurry over cement sand jointing and washing the tiles with cement slurry of matching \color including grinding, rubbing, polishing & mortar cost.(on reception & nursing counter top & wall) | Sft. | 760 | 0 | 0
SURFACE RENDERING
46 | 11-08-b | Cement plaster 1:3 upto 20' height 1/2" thick | 100 Sft. | 19010 | 0 | 0
47 | 11-08-b + 11-26 | Cement plaster 1:3 from 20' to 30' height 1/2" thick | 100 Sft. | 12530 | 0 | 0
48 | 11-08-b +2x(11-26) | Cement plaster 1:3 from 30' to 40' height 1/2" thick | 100 Sft. | 3330 | 0 | 0
49 | 11-08-c | Cement plaster 1:3 upto 20' height 3/4" thick | 100 Sft. | 9500 | 0 | 0
50 | 11-08-c + 11-26 | Cement plaster 1:3 from 20' to 30' height 3/4" thick | 100 Sft. | 5240 | 0 | 0
51 | 11-08-c +2x(11-26) | Cement plaster 1:3 from 30' to 40' height 3/4" thick | 100 Sft. | 3330 | 0 | 0
52 | 11-10-b | Cement plaster 3/8" thick under soffit of RCC roof slabs only upto 20' height : (1:3) | 100 Sft. | 2430 | 0 | 0
53 | 11-10-b +11-26 | Cement plaster 3/8" thick under soffit of RCC roof slabs from upto 20' height to 30' height: (1:3) | 100 Sft. | 2410 | 0 | 0
54 | 11-10-b +2x(11-26) | Cement plaster 3/8" thick under soffit of RCC roof slabs from upto 30' height to 40' height: (1:3) | 100 Sft. | 780 | 0 | 0
55 | 11-30-b | Provide grooved c/s plaster 1:3 over existing plastered & roughened surface 1/2" thick | 100 Sft. | 9500 | 0 | 0
56 | 11-30-b + 11-26 | Provide grooved c/s plaster 1:3 over existing plastered & roughened surface 1/2" thick | 100 Sft. | 5240 | 0 | 0
57 | 11-30-b +2x(11-26) | Provide grooved c/s plaster 1:3 over existing plastered & roughened surface 1/2" thick | 100 Sft. | 3330 | 0 | 0
58 | 11-31 | Provide & fix expanded metal edge bead for corners, with nails on both sides of edges | Rft | 3485 | 0 | 0
WOOD WORK, WOODEN / ALUMINIUM JOINERY
59 | 12-21-b | P/F hydralic door closer (best quality) | Each | 29 | 0 | 0
60 | 12-22-b-02 | Providing and fixing sliding bolt to doors CP sliding bolts : 12" long | Each | 53 | 0 | 0
61 | 12-24-a-01 | Extra for providing / fixing approved quality Rim locks : Imported | Each | 53 | 0 | 0
62 | 12-47 | Supply and Fixing accoustic mineral fibre tile ceiling fixed with aluminium tee hung by GI wire fixed in roof | 100 Sft. | 10300 | 0 | 0
63 | 12-49-b | First class deodar wood wrought joinery in doors and windows etc. panelled or panelled or glazed or fully glazed fixed in position including chowkhat, holdfast, hinges, tower bolt rubber stop cleats/G I clamp, handles and chord with hooks etc. complete (excluding sliding bolts or lock) : 1¾" (45mm) thick. | Sft | 715 | 0 | 0
64 | 12-56-a | Providing and fixing 1.5" (38mm) thick pressed veneered door shutters fully flushed with First class wood veneering on all faces and sides fixed over deodar wood cavited core and frame work of not less than 4" (100mm) wide strips all round with approved brass hinges, tower bolts as required. | Sft | 420 | 0 | 0
65 | 12-58 | 24 SWG aluminium kick plate 4" high, on bottom rail of flush doors of commercial ply | Rft | 300 | 0 | 0
66 | 12-61 | MS flat 1/2"x1/8" grill in windows of approved design | Sft | 1450 | 0 | 0
67 | 12-64-a-06 | Supply and Fixing aluminium door/window, Fixed Glazing Premium model (2.00 mm gauge) 4" section | Sft | 120 | 0 | 0
68 | 12-64-c-05 | Supply and Fixing aluminium door/window, Fly Screen Shutter Premium model (2.00 mm gauge) 2" section | Sft | 765 | 0 | 0
69 | 12-65-a-06 | Supply and Fixing aluminium door/window, Sliding Window Premium model (2.00 mm gauge) 4" section | Sft | 1525 | 0 | 0
70 | 12-65-c-06 | Supply and Fixing aluminium door/window,Hinged Door Premium model (2.00 mm gauge) 4" section | Sft | 695 | 0 | 0
71 | 12-65-f-05 | Supply and Fixing aluminium door/window, Other items Hydraulic Door Closer Double Action | Each | 16 | 0 | 0
72 | 12-70-a | Supply and Fixing MS Sheet 16 guage(10'' x 2'')box type chowkats including fixing in position with all charges for Hold fast, Hinges and Painting etc | Rft | 415 | 0 | 0
73 | 12-78-a | Kitchen floor cabinet as per approved design/ specification (Nurse Room,Nursing Counter, etc.) | Sft | 160 | 0 | 0
74 | 12-78-b | Kitchen wall cabint as per approved design/ specification | Sft | 270 | 0 | 0
PAINTING AND VARNISHING
75 | 13-03-C-01 | Prepare & Paint new surface, doors & windows Priming coat | 100 Sft. | 1010 | 0 | 0
76 | 13-03-c-02 | Prepare & Paint new surface, doors & windows Each subsequent coat of paint | 100 Sft. | 3030 | 0 | 0
77 | 13-06 | Applying lacquer polish to wood work of any type | 100 Sft. | 1715 | 0 | 0
78 | 13-08-a | Bitumen coating to plastered / cement concrete surface : 20 Ibs. per 100 sft. | 100 Sft. | 45010 | 0 | 0
79 | 13-22-a | Preparing surface and painting with emulsion paint : First coat. | 100 Sft. | 4470 | 0 | 0
80 | 13-22-b | Preparing surface and painting with emulsion paint : 2nd & each subsequent coat. (two coats) | 100 Sft. | 8940 | 0 | 0
81 | 13-22-a + 13-24 | Preparing surface and painting with emulsion paint 20' to 30': First coat. | 100 Sft. | 3080 | 0 | 0
82 | 13-22-b + 13-24 | Preparing surface and painting with emulsion paint, from 20' to 30' height: 2nd & each subsequent coat. (two coats) | 100 Sft. | 6160 | 0 | 0
83 | 13-22-a + 2x 13-24 | Preparing surface and painting with emulsion paint 30' to 40': First coat. | 100 Sft. | 1060 | 0 | 0
84 | 13-22-b + 2x 13-24 | Preparing surface and painting with emulsion paint, from 30' to 40' height: 2nd & each subsequent coat. (two coats) | 100 Sft. | 2120 | 0 | 0
85 | 13-25-a | Preparing surface & painting with snowcem / weather shield paint : First coat | 100 Sft. | 200 | 0 | 0
86 | 13-25-b | Preparing surface & painting with snowcem / weather shield paint : 2nd & subsequent coats. | 100 Sft. | 400 | 0 | 0
87 | 13-25-a + 13-24 | Preparing surface & painting with snowcem / weather shield paint 20' to 30': First coat | 100 Sft. | 1950 | 0 | 0
88 | 13-25-b + 13-24 | Preparing surface & painting with snowcem / weather shield paint 20' to30': 2nd & subsequent coats. | 100 Sft. | 3900 | 0 | 0
89 | 14-97 | Supply of 150 Micron Polythene sheet of approved quality | 1 Kg | 127 | 0 | 0
IRON WORK
90 | 25-47 | Supply and fixing of fancy type stainless steel chromium plate 2" dia pipes stair railing 3/4" dia pipe fixed on specified space on steps in horizontal positions, complete in all respects | Rft | 595 | 0 | 0
91 | 25-61 | Supply and fixing of steel door comprising of steel pipe frame of size 1.25" x 2.5" & 1.25" x 2.5" square pipe at lock rail & divider above and below lock rail using 28 SWG plain sheet on both sides including hold fast, hinges & painting complete. | Sft | 98 | 0 | 0
MISCELLANEOUS
92 | 28-15 | Pre anti Termite Treatment in the building mixed with water of mixing ratio as per the manufacturer's certified manual | 100 Sft | 31400 | 0 | 0
93 | 28-18 | Providing and fixing with steel nails and washers, the chicken wire mesh of approved quality, at joint of concrete and masonry work (4" wide strip) before plastering etc complete | Sft | 6250 | 0 | 0
A2. |  | EXTERNAL DEVELOPMENT WORKS (CONCRETE PAVERS)
94 | 03-25-b | Excavation in foundation of building, bridges etc complete: in ordinary soil. | 1000 Cft | 2560 | 0 | 0
95 | 06-05-i | Plain Cement Concrete including placing, compacting, finishing & curing (Ratio 1:4:8) | 100 Cft. | 1280 | 0 | 0
96 | 10-49-f | Providing and Fixing Precast Concrete 3000 psi TUFF Tiles 50mm thick over bed of 2" thick sand | 100 Sft | 5120 | 0 | 0
Cost of Civil Works Scheduled Items (Rs.) | [5 empty] | 0
Add Area factor on KP MRS-2022 (2nd Bi Annual) for District Bannu @ 3% (Rs.) | [5 empty] | 0
Total Cost of Civil Works Scheduled Items (Rs.) | [5 empty] | 0
NON-SCHEDULED ITEMS
A3. |  | BUILDING WORKS
GENERAL NOTE
Supply, installation, testing and commissioning of the following items of work, including all labour, tools, plant, accessories, etc. required for completion of each item as per specifications and as approved by the Engineer.
CONCRETE
(Ref. Specification Section-2300)
97 | NS-01 | Additional cost for using Sulphate Resistant Cement (SRC) in Sub-Structue instead of Ordinary Portland Cement (OPC) (considering 50 kg of bag).If Required | Bags | 5770 | 0 | 0
WATER PROOFING
(Ref. Specification Section-6411)
98 | NS-02 | Water proofing treatment of roof slab comprising one layer of 2mm thick bituminous membrane over primer coated surface as per manufacturers specifications | Sft | 10160 | 0 | 0
99 | NS-03 | Providing and applying 2 coat of Sika seal 105 on floor, complete in all respects and as directed by the Engineer's Incharge. | Sft | 1380 | 0 | 0
100 | NS-04 | Providing and fixing in position 22-SWG. G.I. Flashing (Type-2) bent to shape as given on drawings with 1-1/2" long stainless steel screws @ 18" c/c on one side complete in all respects. | Rft | 540 | 0 | 0
101 | NS-05 | Providing and filling approved sealant in G.I flasing fixed on parapet wall complete. | Rft | 540 | 0 | 0 | 395.46
FLOORING
(Ref. Specification Section-6600)
102 | NS-06 | Providing and application of 3mm-thick. epoxy flooring complete in all respects as shown on drawings or as approved by the Engineer. | Sft | 2650 | 0 | 0
PAINTING AND VARNISHING
(Ref. Specification Section-6700)
103 | NS-07 | 3 coats of Epoxy painting as approved by the Engineer In-Charge on internal wall as mentioned on the drawings and / or as directed by the Engineer In-Charge as per manufacturer's recommendations including supplying all labour, materials, scaffoldings and removal of debris etc. at any floor / height, complete in all respect | Sft | 300 | 0 | 0
104 | NS-08 | 3 coats of Antibacterial painting as approved by the Engineer In-Charge on internal wall as mentioned on the drawings and / or as directed by the Engineer In-Charge as per manufacturer's recommendations including supplying all labour, materials, scaffoldings and removal of debris etc. at any floor / height, complete in all respect | Sft | 25300 | 0 | 0
105 | NS-09 | Colour-creting 1/4" (6.4 mm) thick 1:1:2 (1 white cement mixed with pigment, 1 marble powder and 2 marble chips zero No.) in required shade including dragging the surface with wire brushes complete with curing etc. over a base of 3/4" (19 mm) thick cement plaster 1:3 at any floor / height including the cost of base course as directed complete but excluding the cost of grooves or joints if provided . | Sft | 18050 | 0 | 0
WOOD WORK, WOODEN / ALUMINIUM JOINERY
(Ref. Specification Section-4600,6220)
106 | NS-10 | Supply and fixing of 1 mm Lead lining upto 8ft of all walls over 10 mm PVC foam sheet (water proof) with wooden strip upto ceiling height over PVC paneling up to ceiling height with all required accessories including all fixing accessories i.e. nails, adhesive, reverts, screw, etc. complete in all respects and as directed by the Engineer. | Sft | 3780 | 0 | 0
107 | NS-11 | Supply and fixing of 1.5 mm Lead lining on wooden door with all required fixing accessories i.e. nails, adhesive, reverts, screw, etc. complete in all respects and as directed by the Engineer. | Sft | 265 | 0 | 0
108 | NS-12 | Providing, installation and fixing in poition prefabricated Emergency & OPD Entrance composed of Fire-safe PIR sandwich panels (3" / 80mm thick) of 40Kg/m3 density with supporting system, fittings/fixing accessories as per design and drawings (Covered Area to be measured for payment). | Sft | 530 | 0 | 0
109 | NS-13 | Providing and fixing Fire Rated Door 60 to 90 min Fire Resistance with panic bar with door lock, door handle & closer, complete in all respect. | Job | 3 | 0 | 0
110 | NS-14 | Supply and Fixing of Double Leaf Hermetic Door with Door Frame (Swing Type) Door Leaf: MS, 18 SWG Door Frame: Single Rabbett 16 SWG Door Thickness :42 mm Door Frame: 100mm Vision Panel : 500mm X 500 mm 6 mm Clear Glass with Rubber Seal - PU/Thermopore Infill - Mating Points Highly Finished - Heavy Duty S.S Hinges - Finished with Enemal Paint and including hardware C Type Door Handle, Heavy Duty Door Closer , Bolt Lock Set, Door Seals with all accessories as per manufacturing's specification complete in all respect and as directed be Engineer. | No. | 1 | 0 | 0
111 | NS-15 | Providing and Fixing 0.7mm thick x 067 x 2400mm perforated strip Aluminum ceiling (Brand Talent made in China) with suspension system GI Rafter, wall angle, threaded Rod M6, Anchor bolt M6, Nut M6, Hanger clip, jointing clip, Screws and nail, fixing labor and carriage complete in all respect. | Sft | 6590 | 0 | 0
112 | NS-16 | Providing and fixing in position PVC wall mounted Bumper rail (washable) including cutting and making good and metal lath as per design shown on drawings complete in all respects. | Rft | 980 | 0 | 0
113 | NS-17 | Providing and fixing stainless steel edege protection 2"x2"x6mm-thick on columns and corner dado height straight or curved finishing complete in all respects and as directed by the Engineer's Incharge. | Rft | 940 | 0 | 0
MISCELLANEOUS
ROOM ID SIGNAGE - S1:
114 | NS-18 | Providing, making and fixing Room I.D. Signage comprising of 0.05mm Thick Branded Vinyl Cut-out Letters/Arrows/Pictograms/Caligraphy (color as approved by the architect) to be pasted on Charcoal Grey Nitrocellulose matt coating over 18 mm Thick PVC Foam Board having 1/8" thick Line Separator in Vinyl screwed to Interlocked Aluminum U - channel including sealant, screwed to wall. Complete as per drawings , specifications and as directed by the Consultants/Engineers.
|  | S1 (1'-0" x 0'-5") | No. | 49 | 0 | 0
Department Signage - S2:
115 | NS-19 | Providing, making and fixing Departmental Signage comprising of 0.05mm Thick Branded Vinyl Cut -out Letters/Arrows/ Pictograms/ Caligraphy (color as approved by the architect) to be pasted on Charcoal Grey Nitrocellulose matt coating over 18 mm Thick PVC Foam Board having 1/8" thick Line Separator in Vinyl screwed to Interlocked Aluminum U - channel including sealant, screwed to wall. Complete as per drawings , specifications and as directed by the Consultants/Engineers.
|  | S2 (3'-6" x 0'-5") | No. | 10 | 0 | 0
Ceiling Hung Way Finding Signage - S3:
116 | NS-20 | Providing, making and fixing Ceiling Hung Way Finding Signage (Two Way) comprising of 0.05mm Thick Branded Vinyl Cut-out Letters/ Arrows/Pictograms/Caligraphy in white color to be pasted on Charcoal Grey Nitrocellulose matt coating over 18 mm Thick PVC Foam Board with chamfered edges having 1/8" thick Line Separator in Vinyl. The PVC Foam Board to be screwed to all sides of 16 SWG M.S. framing welded to 12mm Dia S.S. pipe in brushed finish screwed to 3mm thick steel plate bolted to existing R.C.C Slab. Complete as per drawings, specifications and as directed by the Consultants/ Engineers.
|  | S3 (Size varies) | Sft | 17.555 | 0 | 0
Wall Hung Way Finding Signage - S4:
117 | NS-21 | Providing, making and fixing Signage comprising of 0.05mm Branded Thick Vinyl Cut -out Letters/ Arrows/Pictograms/Caligraphy (Color As Approved by the Architect) to be pasted on 0.05mm Thick Matt 80% Grey vinyl base to be pasted on 25mm Thick PVC Foam Board plate having chamfered edges as top of signage panel and remaining panels are to be pasted on Charcoal Grey Nitrocellulose matt coating over 18 mm Thick PVC Foam Board with chamfered edges having 1/8" thick Line Separator in Vinyl screwed to Interlocked Aluminum U - channel including sealant, screwed to wall. Complete as per drawings , specifications and as directed by the Consultants/Engineers.
|  | S4 (Size varies) | Sft | 15.19 | 0 | 0
Ceiling Hung Building Directory Signage- S5:
118 | NS-22 | Providing, making and fixing Signage comprising of 0.05mm Thick Branded Vinyl Cut -out Letters/ Arrows/Pictograms/Caligraphy (Color As Approved by the Architect) to be pasted on Charcoal Grey Nitrocellulose matt coating over 18 mm Thick PVC Foam Board with chamfered edges having 1/8" thick Line Separator in Vinyl. The PVC Foam Board to be screwed to all sides of 16 SWG M.S. framing welded to 12mm Dia S.S. pipe in brushed finish screwed to 3mm thick steel plate bolted to existing R.C.C Slab. Complete as per drawings, specifications and as directed by the Consultants/ Engineers.
|  | S5 (Size varies) | Sft | 19.92 | 0 | 0
Stair ID Signage - S6:
119 | NS-23 | Providing, making and fixing Signage comprising of 0.05mm Thick Branded Vinyl Cut-out Letters/Arrows/Pictograms/Caligraphy (color as approved by the architect) to be pasted on Charcoal Grey Nitrocellulose matt coating over 18 mm Thick PVC Foam Board having 1/8" thick Line Separator in Vinyl screwed to Interlocked Aluminum U - channel including sealant, screwed to wall. Complete as per drawings , specifications and as directed by the Consultants/Engineers.
|  | S5 (2'-0" x 0'-10") | No. | 10 | 0 | 0
Lift ID Signage - S7:
120 | NS-24 | Providing, making and fixing Signage comprising of 0.05mm Thick Branded Vinyl Cut-out Letters/Arrows/Pictograms/Caligraphy (color as approved by the architect) to be pasted on Charcoal Grey Nitrocellulose matt coating over 18 mm Thick PVC Foam Board having 1/8" thick Line Separator in Vinyl screwed to Interlocked Aluminum U - channel including sealant, screwed to wall. Complete as per drawings , specifications and as directed by the Consultants/Engineers.
|  | S7 (2'-0" x 0'-10") | No. | 8 | 0 | 0
Wall Flag Signage - S8:
121 | NS-25 | Providing, making and fixing (Two Way) Signage comprising of 0.05mm Thick Branded Vinyl Cut out Letters/Arrows/Pictograms/ Caligraphy (color as approved by the architect) to be pasted on Charcoal Grey Nitrocellulose matt coating over 18 mm Thick PVC Foam Board having 1/8" thick Line Separator in Vinyl screwed to Interlocked Aluminum U - channel including sealant, screwed to wall. Complete as per drawings , specifications and as directed by the Consultants/Engineers.
|  | S8 (1'-0" x 0'-5") | No. | 44 | 0 | 0
Emergency Department Signage - S11:
122 | NS-26 | Providing, making and fixing of Emergency department Signage comprising of Aluminum Fame with Alumnium Cutouts Backlit Letters with LED lights including fixing arrangements and all civil works Complete as per drawings , specifications and as directed by the Consultants/Engineers.
|  | S11 (Size Varies) Min. 12' in length | Sft | 24 | 0 | 0
Bed Number Signage - S12:
123 | NS-27 | Providing, making and fixing Bed Number Signage comprising of 0.05mm Thick Branded Vinyl Cut-out Letters/Arrows/Pictograms/ Caligraphy (color as approved by the architect) to be pasted on Charcoal Grey Nitrocellulose matt coating over 18 mm Thick PVC Foam Board having 1/8" thick Line Separator in Vinyl screwed to Interlocked Aluminum U - channel including sealant, screwed to wall. Complete as per drawings , specifications and as directed by the Consultants/Engineers.
|  | S12 (0'-6" x 0'-6") | No. | 38 | 0 | 0
Cost of Civil Works Non-Scheduled Items (Rs.) | [5 empty] | 0 | 0
Grand Total Cost of Civil Works Scheduled Items & Non-Scheduled Items (Rs.) | [5 empty] | 0

## 2. Electrical
UNHCR PAKISTAN
CONSTRUCTION OF CCU BLOCK AT DISTRICT HEADQUARTER HOSPITAL, BANNU
ENGINEER'S ESTIMATE
ELECTRICAL WORKS
ITEM No. | KPK MRS 2022 REF. NO. / NS (2nd BI ANNUAL) | DESCRIPTION | UNIT |  | QTY | UNIT RATE (Rs.) | TOTAL AMOUNT (Rs.)
(a) | (b) | (c) | (d) |  | (e) | (f) | (g)
B1. |  | BUILDING ELECTRICAL WORKS
SCHEDULED ITEMS
FANS & EXHAUST FANS
1 | 15-68-c | Supply and Erection best quality AC ceiling fan complete with GI rod, canopy, blades & regulator: 56" sweep. | 1 | Each | 75 | 0 | 0
2 | 15-69-a | Supply & Erection best quality exhaust fan complete with shutter & regulator: 12" sweep. | 1 | Each | 20 | 0 | 0
3 | 15-77-c | Supply and Fixing electric AC exhuast/fresh air circulation(double way) 220/230 single phase plastic frame body and blade complete 12"x12" | 1 | Each | 2 | 0 | 0
4 | 15-67 | Making hole in wall with necessary masonry work for exhaust fan any size complete | 1 | Each | 22 | 0 | 0
5 | 15-78 | Supply and Fixing of 18" dia Direct axial Wall Bracket fan,1450Rpm, Max 50db sound level Fan shall be made with 99% purity Copper windings | 1 | Each | 5 | 0 | 0
6 | 15-25 | Supply and Erection girder clamp hook, 5/8" dia.for hanging ceiling fans. | 1 | Each | 75 | 0 | 0 | 260000 | 0
NOTE:The contractor/supplier shall ensure that the supplied fans are wound with pure 99.9% pure enamelled copper winding.The core of the fans shall be made from grain oriented electrical steel sheet.The exhaust fans shall follow the same standards described above. Moreover all fans should be NEECA approved.The fans shall be installed at the bottom level of structural beams. The contractor is required to get the approval from the site staff.
LT CABLES
7 | 15-122-g | Supply at site, installation, testing and commissioning of PVC insulated un-armoured copper conductor cable 600 / 1000 Volt grade (or otherwise mentioned in cable description ) in prelaid conduits / trenches to be installed as per routes shown on drawings including cost of all necessary materials, connections, identification tags, cables lugs properly crimped at both ends for the following sizes complete in all respects. (4 core 70 sqmm) | 1 | RM | 30 | 0 | 0
8 | 15-122-f | Supply at site, installation, testing and commissioning of PVC insulated un-armoured copper conductor cable 600 / 1000 Volt grade (or otherwise mentioned in cable description ) in prelaid conduits / trenches to be installed as per routes shown on drawings including cost of all necessary materials, connections, identification tags, cables lugs properly crimped at both ends for the following sizes complete in all respects (50 sqmm, 4 core ) for Power DB | 1 | RM | 10 | 0 | 0
9 | 15-122-e | Supply at site, installation, testing and commissioning of PVC insulated un-armoured copper conductor cable 600 / 1000 Volt grade (or otherwise mentioned in cable description ) in prelaid conduits / trenches to be installed as per routes shown on drawings including cost of all necessary materials, connections, identification tags, cables lugs properly crimped at both ends for the following sizes complete in all respects (35 sqmm, 4 core) | 1 | RM | 25 | 0 | 0
10 | 15-122-d | Supply at site, installation, testing and commissioning of PVC insulated un-armoured copper conductor cable 600 / 1000 Volt grade (or otherwise mentioned in cable description ) in prelaid conduits / trenches to be installed as per routes shown on drawings including cost of all necessary materials, connections, identification tags, cables lugs properly crimped at both ends for the following sizes complete in all respects (25 sqmm, 4 core ) | 1 | RM | 25 | 0 | 0
11 | 15-122-c | Supply at site, installation, testing and commissioning of PVC insulated un-armoured copper conductor cable 600 / 1000 Volt grade (or otherwise mentioned in cable description ) in prelaid conduits / trenches to be installed as per routes shown on drawings including cost of all necessary materials, connections, identification tags, cables lugs properly crimped at both ends for the following sizes complete in all respects (16 sqmm, 4 core ) | 1 | RM | 5 | 0 | 0
12 | 15-122-b | Supply at site, installation, testing and commissioning of PVC insulated un-armoured copper conductor cable 600 / 1000 Volt grade (or otherwise mentioned in cable description ) in prelaid conduits / trenches to be installed as per routes shown on drawings including cost of all necessary materials, connections, identification tags, cables lugs properly crimped at both ends for the following sizes complete in all respects (10 sqmm, 4 core) For Lights DB | 1 | RM | 25 | 0 | 0
13 | 15-122-a | Supply at site, installation, testing and commissioning of PVC insulated un-armoured copper conductor cable 600 / 1000 Volt grade (or otherwise mentioned in cable description ) in prelaid conduits / trenches to be installed as per routes shown on drawings including cost of all necessary materials, connections, identification tags, cables lugs properly crimped at both ends for the following sizes complete in all respects (6 sqmm, 4 core ) (for pumps). | 1 | RM | 30 | 0 | 0
14 | 15-07-e | Supply and Erection single core PVC insulated & sheathed copper conductor, 660/1100V cable : 37/0.072 (95mm2) | 1 | RM | 10 | 0 | 0
15 | 15-07-d | Supply and Erection single core PVC insulated & sheathed copper conductor, 660/1100V cable : 19/0.083" (70mm2) | 1 | RM | 100 | 0 | 0
16 | 15-07-c | Supply and Erection single core PVC insulated & sheathed copper conductor, 660/1100V cable : 19/0.064" (35mm2 as ECC) | 1 | RM | 10 | 0 | 0
17 | 15-07-b | Supply and Erection single core PVC insulated & sheathed copper conductor, 660/1100V cable : 19/0.052" (25mm2 as ECC) | 1 | RM | 10 | 0 | 0
18 | 15-06-f | Supply and Erection single core PVC insulated+sheathed copper conductor 250/440 V grade cable : 7/0.064" (16mm2 as ECC) | 1 | RM | 30 | 0 | 0
19 | 15-06-e | Supply and Erection single core PVC insulated+sheathed copper conductor 250/440 V grade cable : 7/0.044" (6mm2 as ECC) | 1 | RM | 20 | 0 | 0
20 | 15-124-a | Supply and Erection of 2 X 10 sqmm copper cable | 1 | RM | 10 | 0 | 0
21 | 15-126-a | Supply at site, installation, testing and commissioning of PVC insulated un-armoured copper conductor cable 600 / 1000 Volt grade (or otherwise mentioned in cable description ) in prelaid conduits / trenches to be installed as per routes shown on drawings including cost of all necessary materials, connections, identification tags, cables lugs properly crimped at both ends for the following sizes complete in all respects (10sqmm, 1 core ) . | 1 | RM | 10 | 0 | 0
CONDUITS & PIPES
22 | 15-02-b-06 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 2" i/d | 1 | Rft. | 550 | 0 | 0
23 | 15-02-b-05 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 1.5" i/d | 1 | Rft. | 30 | 0 | 0
24 | 15-79-a | Supply and Fixing PVC conduit for surface wiring (duraduct) 1/2" including all charges for nail screws etc | 1 | Rft. | 50 | 0 | 0
25 | 15-79-b | PVC conduit for surface wiring (duraduct) 1" including all charges for nail screws etc | 1 | Rft. | 50 | 0 | 0
26 | 15-79-c | PVC conduit for surface wiring (duraduct) 1.5" including all charges for nail screws etc | 1 | Rft. | 50 | 0 | 0
27 | 15-79-d | PVC conduit for surface wiring (duraduct) 2" including all charges for nail screws etc | 1 | Rft. | 50 | 0 | 0
28 | 24-18-c-05 | Providing, laying, cutting, jointing, testing and disinfecting UPVC pressure pipeline in trenches (conforming to BS 3505 manufactured ) jointed with socket, elbow, tee, bend and plug bend etc.manufactured by the respective manufacturer complete as per specifications. uPVC Pressure Pipes Class D (12 Bar) 3" Nominal Pipe Size (NPS) | 1 | Rft. | 1500 | 0 | 0
29 | 24-18-c-03 | Providing, laying, cutting, jointing, testing and disinfecting UPVC pressure pipeline in trenches (conforming to BS 3505 manufactured) jointed with socket, elbow, tee, bend and plug bend etc. manufactured by the respective manufacturer complete as per specifications. uPVC Pressure Pipes Class D (12 Bar) 2"Nominal Pipe Size (NPS) | 1 | Rft. | 500 | 0 | 0
WIRING ACCESSORIES
30 | 15-127-a | Supply at site, installation, testing and commissioning of the One gang light control switches 10 Amps, 250 Volts one way, including appropriate size concealed MS, powder coated back box, complete in all respects. | 1 | No. | 12 | 0 | 0
31 | 15-127-b | Supply at site, installation, testing and commissioning of Two gang light control switches 10 Amps, 250Volts one way, including appropriate size concealed MS, powder coated back box, complete in all respects. | 1 | No. | 60 | 0 | 0
32 | 15-127-c | Supply at site, installation, testing and commissioning of Three gang light control switches 10 Amps, 250Volts one way, including appropriate size concealed MS, powder coated back box, complete in all respects. | 1 | No. | 30 | 0 | 0
33 | 15-127-d | Supply at site, installation, testing and commissioning of Four gang light control switches 10 Amps, 250 Volts one way, including appropriate size concealed MS, powder coated back box, complete in all respects. | 1 | No. | 60 | 0 | 0
34 | 15-127-e | Supply at site, installation, testing and commissioning of Five gang light control switches 10 Amps, 250 Volts one way, including appropriate size concealed MS, powder coated back box, complete in all respects. | 1 | No. | 15 | 0 | 0
35 | 15-127-f | Supply at site, installation, testing and commissioning of Six gang light control switches 10 Amps, 250 Volts one way, including appropriate size concealed MS, powder coated back box, complete in all respects | 1 | No. | 15 | 0 | 0
36 | 15-127-h | Supply at site, installation, testing and commissioning of One gang light control switches 10 Amps, 250Volts two way, including appropriate size concealed MS, powder coated back box, complete in all respects | 1 | No. | 12 | 0 | 0
37 | 15-156 | Supply, Installation, Connecting, testing and commissioning of 400 watt Fan dimmer, polycarbonate flame retardant with fancy gang plate fixed on die fabricated poweder coated metal board recessed in wall or column , Complete in all respects | 1 | No. | 75 | 0 | 0
38 | 15-155-c | Supply, installation, connecting, testing & commissioning of flush type 13 Amps 3-pin simplex outlet with 3 pin switch and socket combine unit with neon bulb fixed on plastic or fiber top covered, including 14 SWG metal board with earth | 1 | No. | 280 | 0 | 0
39 | 15-127-j | Supply at site, installation, testing and commissioning of 3 pin switched socket unit 13/15 Amps, 250Volts, round pin including appropriate size MS, powder coated back box, complete in all respects. | 1 | Each | 20 | 0 | 0
40 | 15-127-n | Supply at site, installation, testing and commissioning of DP switch 20 Amps with neon indication lamp complete with MS, powder coated back box, complete in all respects. | 1 | Each | 45 | 0 | 0
WIRING IN CONCEALED CONDUITS
41 | 15-06-a | Supply and Erection single core PVC insulated+sheathed copper conductor 250/440 V grade cable : 3/0.029"(1.5mm2). | 1 | Rft | 33000 | 0 | 0
42 | 15-06-c | Supply and Erection single core PVC insulated+sheathed copper conductor 250/440 V grade cable : 7/0.029"(2.5mm2) . | 1 | Rft | 28000 | 0 | 0
43 | 15-06-d | Supply and Erection single core PVC insulated+sheathed copper conductor 250/440 V grade cable : 7/0.036"(4mm2) . | 1 | Rft | 30000 | 0 | 0
44 | 15-06-e | Supply and Erection single core PVC insulated+sheathed copper conductor 250/440 V grade cable : 7/0.044"(6mm2) . | 1 | Rft | 1000 | 0 | 0
45 | 15-02-b-03 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 1" i/d (for wiring) | 1 | Rft. | 10000 | 0 | 0
46 | 15-02-b-02 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 3/4" i/d (for wiring) | 1 | Rft. | 30000 | 0 | 0
NOTE: The wiring shall be done as following.
| a | Wiring of light circuit from Distribution Board to switch, including circuit wiring between switches on the same circuit with Two nos. single core 2.5 Sqmm and One no.1.5 sq mm PVC insulated 300/500 Volts grade stranded copper conductor cables in concealed 1 " PVC conduits including PVC conduit, conduit accessories (junction box, pull box, metal fan box etc) complete in all respects.
| b | Wiring from switch to light or fan point (1 way / 2 way) with 3 Nos. single core 1.5 Sqmm PVC insulated 300/500 Volts grade stranded copper conductor cables in concealed 1" PVC conduit including PVC conduit, conduit accessories (junction box, pull box, metal fan box etc) complete in all respects.
| c | Wiring from light to light with 3 Nos. single core 1.5 Sqmm PVC insulated 300/500 Volts grade stranded copper conductor cables in concealed 3/4" PVC conduit including PVC conduit, conduit accessories (junction box, pull box, metal fan box etc) complete in all respects.
| d | Wiring of circuit from Distribution Board to 13A , 230 Volts, 3 pin switched socket outlet with Two nos. single core 4 sqmm and One no. 2.5 sqmm PVC insulated 300/500 Volts grade stranded copper conductor cables in 1" dia concealed PVC conduit laid underfloor including PVC conduit, conduit accessories, etc. complete in all respects.
| e | Wiring from 13 Amps, 3 pin socket to socket with Two nos. single core 2.5 Sqmm and One no. 1.5 sq mm PVC insulated 300/500 Volts grade stranded copper conductor cables in concealed 1" PVC conduit laid underfloor including PVC conduit, conduit accessories, etc.complete in all respects.
| f | Wiring of circuit from distribution board to 15A, 230 Volts, 3 Pin switched socket outlet with 2 Nos. one core 4 Sqmm and One no. 2.5 sq mm PVC insulated 300/500 Volts grade copper conductor cables in concealed 1" PVC conduit laid underfloor including PVC conduit, conduit accessories, etc. complete in all respects.
| g | Wiring from 15 Amps, 3 pin socket to socket with Two nos. single core 2.5 Sqmm and One no. 1.5 sq mm PVC insulated 300/500 Volts grade stranded copper conductor cables in concealed 1" PVC conduit laid underfloor including PVC conduit, conduit accessories, etc.complete in all respects.
| h | Wiring of circuit from distribution board to 20A, 230 Volts, switched socket outlet with 2 Nos. one core 4 Sqmm and One no. 2.5 sq mm PVC insulated 300/500 Volts grade stranded copper conductor cables in concealed 1" PVC conduit laid underfloor including PVC conduit, conduit accessories, etc. complete in all respects (For ACs).
| i | Wiring of circuit from distribution board to 20A, 230 Volts, switched socket outlet with 2 Nos. one core 6 Sqmm and One no. 2.5 sq mm PVC insulated 300/500 Volts grade stranded copper conductor cables in concealed 1" PVC conduit laid underfloor including PVC conduit, conduit accessories, etc. complete in all respects (For Electric Water heaters).
NOTE: PVC pipes & all its accessories shall not catch/support fire. 1.5mm2 (3/0.029) & 2.5mm2 (7/0.029) single core cables are stranded having 3 strands & 7 strands respectively.
FIRE ALARM SYSTEM
47 | 15-131-d | Supply, installation, testing & commissioning of Analogue Addressable Optical Smoke Detector with Base; 24 VDC; UL LISTED, low voltage, solid state, Not Radio Active type, uni-polar and dual chamber with LED alarm indication to be installed on RCC slab, complete in all respects | 1 | Each | 46 | 0 | 0
48 | 15-131-e | Supply, installation, testing & commissioning of Addressable Heat Detector | 1 | Each | 2 | 0 | 0
49 | 15-131-b | Supply, installation, testing & commissioning of Analogue Addressable Manual Call Point / Pull Station with Base and Back Box with Key UL Listed complete in all respects. | 1 | Each | 6 | 0 | 0
50 | 15-131-c | Supply, installation, testing & commissioning of Analogue Addressable Sounder with Flasher, 24 VDC, Mounting Base and with Base and Back Box with Key UL Listed complete in all respects. | 1 | Each | 6 | 0 | 0
51 | 15-131-a | Supply, testing and commissioning of 2 core 1.5mm. Sqmm stranded copper conductor tin coated with drain PVC insulated wires 600/1000 V. grade, fire resistant, LSZH Cu Conductor to be pulled in already installed 20mm dia. heavy duty PVC conduit recessed in wall, columns, slab, floor or above false ceiling with all necessary fixing accessories as per site conditions | 1 | Point | 60 | 0 | 0
LIGHT FIXTURES
52 | 15-36-k-02 | Supply, installation, connecting, testing and commissioning of Surface mounting LED tube light with 1x2000 lumens output and fixture, complete in all respects | 1 | No. | 12 | 0 | 0
53 | 15-36-i-10 | Supply, installation, testing and commissioning of 1x6 Watt LED BULKHEAD light fixture, of best quality. | 1 | Each | 45 | 0 | 0
54 | 15-36-i-7 | Supply, installation, testing and commissioning of 1x23 Watt, E-27 base, wall bracket light, complete in all respects. | 1 | Each | 5 | 0 | 0
55 | 15-36-j-12 | Supply, installation, connecting, testing & commissioning of 10W LED Down Light Fixture suitable for 1300 lux, as per instruction of Engineer, surface mounted circular shape or equivalent | 1 | No. | 200 | 0 | 0
PUBLIC ADDRESS SYSTEM
56 | 15-130-a | Supply, installation, testing and commissioning of 2 core 1.5 Sqmm stranded copper conductor tin coated with drain PVC insulated wires 600/1000 V. grade, fire resistant, low smoke, zero halogen Cu conductor to be pulled in already installed 20mm dia. heavy duty PVC conduit recessed in wall, columns, slab, floor or above false ceiling with all necessary fixing accessories | 1 | Point | 70 | 0 | 0
57 | 15-130-i | Supply, installation, testing & commissioning of Ceiling Mount Speakers | 1 | Each | 20 | 0 | 0
58 | 15-130-b | Supply, installation, testing and commissioning of Mixer Amplifier (240W); 6 MIC Input; complete in all respects | 1 | Each | 1 | 0 | 0
59 | 15-130-e | Supply, installation, testing & commissioning of Back Ground Music Player | 1 | Each | 1 | 0 | 0
60 | 15-130-f | Supply, installation, testing & commissioning of Goose Neck Microphone | 1 | Each | 1 | 0 | 0
61 | 15-138-g | Supply and Erection of 3M Cat-6 Cable in 3/4",1"pvc conduit, complete in all respect (from call station to voice controller) | 1 | Rft | 600 | 0 | 0
STRUCTURED CABLING SYSTEM (TELEPHONE & NETWORKING)
62 | 15-138-e-01 | Supply, Installation, testing and commissioning of Single Port Data outlet of 1 x RJ-45 I/Os for Cat-6 cable and with 16 SWG back box, complete in all respects | 1 | Each | 75 | 0 | 0
63 | 15-138-g | Supply and Erection of 3M Cat-6 Cable in 3/4",1"pvc conduit, complete in all respect | 1 | Rft | 11000 | 0 | 0
64 | 15-141-a | Supply, installation, testing and commissioning of Cable Manager / Organizer Black, 1pc, Black. | 1 | Each | 5 | 0 | 0
65 | 15-145 | Supply, installation, testing and commissioning of the ODF; 12 Port Loaded with 6x Pigtails Multimode Tray & Other Accessories, Rack Mount 1U Form Factor, complete in all respects. (floor distribution). | 1 | No. | 2 | 0 | 0
66 | 15-143-b | Supply, installation, testing and commissioning of the following Fiber Optic Cables to be installed in conduits, cable trays and dura duct including cost of all necessary accessories/ materials complete in all respects. (floor distribution). | 1 | Rft | 600 | 0 | 0
MISCELLANEOUS ITEMS
67 | 15-178 | Supply & Erection of TV socket | 1 | Each | 6 | 0 | 0
68 | 15-175 | Supply & Erection of TV/satellite cable complete | 1 | Each | 6 | 0 | 0
69 | 15-135-b | Supply at site, fabrication and installation of GI perforated cable tray 16 SWG 8 ft. to 10 ft. long with sides 3" high to be installed on wall, or in vertical, or above false ceiling in horizontal position or floor mounted or as shown on drawing, including cost of hanging arrangement brackets made of angle iron 38mm x 38mm x 6mm installed at every 3 ft., cost of all necessary fixing accessories, complete in all respects.(300X100mm) | 1 | Rft. | 100 | 0 | 0
B2. |  | EXTERNAL ELECTRICAL WORKS
CIVIL WORKS FOR CABLES
70 | 03-51 | Excavation of trench in all kinds of soils except cutting in rock for pipelines upto 1.5m depth (for electrical cables) | 1 | 1000 Cft | 3000 | 0 | 0
71 | 03-67-c | Structural backfill using Common Material available at site. | 1 | 1000 Cft | 3000 | 0 | 0
72 | 07-30 | Supplying and filling sand under floor or plugging in wells | 1 | 100 Cft | 3000 | 0 | 0
NOTE:
The above items must be executed as follows:
| a) | Excavation in all kind of material including back filling, compaction, layer of bricks 9" in width and warning tape for lighting cables trench width 3' & height 4' complete in all respect as per specifications and as directed by the Engineer .
CABLE PULLING PIT ( 4'x4'x4')
73 | 03-49-a | Excavation in open cut for sewers & manhole except shingle, gravel & rock : Upto 2m (for electrical works) | 1 | 1000 Cft | 150 | 0 | 0
74 | 03-67-c | Structural backfill using Common Material available at site. | 1 | 1000 Cft | 150 | 0 | 0
75 | 06-05-i | Plain Cement Concrete incl. placing, compacting, finishing & curing (Ratio 1:4:8) | 1 | 100 Cft | 10 | 0 | 0
76 | 06-07-a-03 | RCC in roof slab, beam, column & other structural members, insitu or precast. Type C (1:2:4) | 1 | 100 Cft | 50 | 0 | 0
77 | 06-08-c | Supply & fabricate M.S. reinforcement for cement concrete (Hot rolled deformed bars Grade 40) | 1 | 100 Kg | 113.4301 | 0 | 0
78 | 11-08-b | Cement plaster 1:3 upto 20' height 1/2" thick | 1 | 100Sft | 72 | 0 | 0
79 | 07-30 | Supplying and filling sand under floor or plugging in wells | 1 | 100 cft | 150 | 0 | 0
80 | 24-33-d | Supplying and fixing, cast iron manhole cover with frame, etc. (Heavey Type) of approved quality complete. 24" (600 mm) dia | 1 | Each | 3 | 0 | 0
NOTE:
The above items must be executed as follows:
| a | Cable pulling pit (4'-0" X 4'-0" X 4') made of RCC walls(1:2:4) and CI cover with MS angle frame for easy pulling of LT cables and telephone/networking cables including all accessories located as per drawings.
CONDUITS & PIPES
81 | 24-18-c-06 | Providing, laying, cutting, jointing, testing and disinfecting UPVC pressure pipeline in trenches (conforming to BS 3505 manufactured ) jointed with socket, elbow, tee, bend and plug bend etc.manufactured by the respective manufacturer complete as per specifications. uPVC Pressure Pipes Class D (12 Bar) 4" Nominal Pipe Size (NPS) | 1 | Rft. | 3000 | 0 | 0
LT CABLES
82 | 15-07-g | Supply and Erection single core PVC insulated & sheathed copper conductor, 660/1100V cable : 37/0.103"(185 mm2) Transformer to Main Panel | 1 | RM | 1100 | 0 | 0
Cost of Building Electrical works Scheduled Items (Rs.) | [6 empty] | 0
Add Area factor on KP MRS-2022 (2nd Bi Annual) for District Bannu @ 3% (Rs.) | [6 empty] | 0
Total Cost of Building Electrical works Scheduled Items (Rs.) | [6 empty] | 0
NON-SCHEDULED ITEMS
B3. |  | BUILDING WORKS
Supply, installation, testing and commissioning of the following items of work, including all labour, tools, plant, accessories, etc. required for completion of each item as per specifications and as approved by the Engineer.
LT DISTRIBUTION BOARD
(Ref. Specification Section-8001, 8133)
LT 415V AC Main DB/Sub-Main DBs shall be made from 14 SWG sheet steel, while all other DBs must be of 16SWG. This shall be designed, fabricated and manufactured as a free standing floor type. The sheet metal work shall be cleaned down to bare shining metal degreased, derusted and painted with TWO base coats of antirust RED paint. The sheet metal work shall be finished in TWO coats of powder paint. The color and shade shall be as approved by the Engineer. The distribution Board shall be complete with all internal wirings, tags, identification labels, TPN and E copper busbars, accessories etc. The DB should be provided with the armored glands. The bus-bars shall be insulated in RED, YELLOW, BLUE and BLACK insulations. The insulation shall be heat shrinkable type or as directed by the Engineer.
83 | NS-01 | MDB | 1 | Job | 1 | 0 | 0
84 | NS-02 | EMDB | 1 | Job | 1 | 0 | 0
85 | NS-03 | SMDB-UPS | 1 | Job | 1 | 0 | 0
86 | NS-04 | LDB- GF | 1 | Job | 1 | 0 | 0
87 | NS-05 | LDB- FF | 1 | Job | 1 | 0 | 0
88 | NS-06 | PDB-GF | 1 | Job | 1 | 0 | 0
89 | NS-07 | PDB-FF | 1 | Job | 1 | 0 | 0
90 | NS-08 | ACDB-GF | 1 | Job | 1 | 0 | 0
91 | NS-09 | ACDB-FF | 1 | Job | 1 | 0 | 0
92 | NS-10 | PDB-MF | 1 | Job | 1 | 0 | 0
93 | NS-11 | PDB-CL | 1 | Job | 1 | 0 | 0
NOTE: Cable Glands should be of non-magnetic material i.e. Stainless Steel or Aluminum
LIGHT FIXTURES
(Ref. Specification Section-8001, 8150)
Following light fixtures installed on surface or wall or floor or false ceiling or columns or masts complete with all accessories such as lamps, lamp holders, ballasts, starters, ignitors, capacitors, LED drivers as applicable, etc. including all relevant installation material as required and approved by the Engineer. (Note: The contractor shall be reponsible for compatibility of recessed mounted light fixtures with gypsum / aluminium / dampa etc., false ceiling types in coordination with architectural design.)
94 | NS-12 | Surface mounted LED batten Light Fixture (600mm) with minimum 800 lumens , fixed output LED driver and prismatic diffuser, IP20 rated (To be used in Toilets vanities). | 1 | No. | 20 | 0 | 0
95 | NS-13 | Surface/Recessed Panel type LED light fixture (600mm by 600 mm) suitable for 2' x 2' false ceiling with minimum 3700 lumens IP20 rated. | 1 | No. | 160 | 0 | 0
WIRING ACCESSORIES
(Ref. Specification Section-8001, 8220)
Supply and Installation of following types of socket outlets including Face Plate, sheet steel back box made of 16 SWG finished in powder coated paint and all accessories, complete in all respects.
96 | NS-14 | 16 Amps, 400 Volts Four Pole on-off switch(3P Switch+ADD-On Fourth Pole), direct operating and door coupling control with all mounting accessories complete in all respects . | 1 | No. | 1 | 0 | 0
97 | NS-15 | Weather Protected transparent Covers for 15Amp socket (For water coolers). | 1 | No. | 1 | 0 | 0
STRUCTURED CABLING SYSTEM (TELEPHONE & NETWORKING)
(Ref. Specification Section-8001, 8312)
98 | NS-16 | Supply, Installation & Connecting up of UTP- Cat-6,steel Frame Patch Panel with 24 port modular UTP - Cat-6, Loaded with BLUE CAT I/O UTP , Keystone Jacks Toolless, Support 1.0 Gigabit Network including rear cable management | 1 | No. | 6 | 0 | 0
99 | NS-17 | Supply, Installation of UTP - Cat-6, Patch Cords Support 1.0 Giga Network at 250 Mhz machine made. Installed between patch panel & Network switch and face plate
| i) | 1.0 m Length | 1 | No. | 50 | 0 | 0
| ii) | 3.0 m Length | 1 | No. | 50 | 0 | 0
100 | NS-18 | Supply, Installation of wall mounted 6U (600 x 550mm) data cabinet imported, double section, including fans with lockable front glass door two side opening, 04 Way power distribution unit rack mounted IP 20. | 1 | No. | 1 | 0 | 0
101 | NS-19 | Supply ,Installation of 42U 800X1000mm Imported,Perforated Cabinet with two vertically mounted PDU 32A,220V in Rear and 2 Vertical Cable Managers in Front ,Including Fan Units Ip-20 Rated , Cold Rolled Steel Cabinet (MAIN SERVER ROOM) | 1 | Each. | 1 | 0 | 0
IP CCTV SYSTEM
(Ref. Spec. Nos. 8001, 8335)
102 | NS-20 | Supply at site, installation, testing & commissioning of Network TDN WDR IR Rugged Dome/Bullet Camera, 1/2.9" CMOS, 4 MP, 2.7-12mm MFZ, 4 High Power LEDs,VARIFOCAL DC IRIS NS, PoE, H.264, microSD, 128 GB max, IP 54 or better,IK 10, built in cyber security feature including mounting bracket, all fixing and mounting accessories, complete in all respects., complete in all respects. | 1 | Each | 30 | 0 | 0
MISCELLANEOUS ITEMS
(Ref. Specification Section-8001, 8290)
103 | NS-21 | Providing & fixing Ceiling mounted 12' Exhaust fans along with exhaust pipe complete with all accessories complete in al respect as approved by the Engineer. | 1 | No. | 8 | 0 | 0
104 | NS-22 | Supply, Installation of 1-to-12 Ports TV Cable Splitter | 1 | No. | 1 | 0 | 0
105 | NS-23 | Providing & fixing Floor Box for (4 face plates of 3" x 3") as approved by the Engineer.make Legrand or Equivalent | 1 | No. | 5 | 0 | 0
106 | NS-24 | Providing & fixing 6 Amps plastic ceiling rose on PVC Round block/Round Cover fitted on surface including connection as required. | 1 | No. | 1 | 0 | 0
107 | NS-25 | Providing and fixing circular recessed type false ceiling fan having size of 2' x 2' made of plaastic body complete with speed control remote, shoe, cord, etc. complete in all respect i/c connection with 14.0076" flexible wire as required. (Pak/ Royal or approved equivalent) | 1 | no. | 20 | 0 | 0
108 | NS-26 | Bed Head Unit, with 3 Nos. 13Amp power socket and 3 Nos. points for oxygen system | 1 | Each | 45 | 0 | 0
FIRE ALARM SYSTEM
(Ref. Specification Section-8001, 8331)
109 | NS-27 | Intelligent Addressable Fire Alarm Control Panel (2-Loop), Wall Mount, Microprocessor Based, Lcd Display, Multi-Function Status Leds, 127 Devices / Elements Per Loop , Network Able Via 2-Core Copper Cable & Cat-VI Cable Simultaneously Upto A Range Of 40 Km on Single Mode Optical Fiber, Graphical User Interface Support, Remotely Programmable, Free Of Cost Programming Software, Input/Output Interfacing, Multi Configuration Level, 24 Hours Back Up Time & 30 Minutes Alarm Time. | 1 | Job | 1 | 0 | 0
ACCESS CONTROL SYSTEM
(Ref. Spec. Sec. 8001, 8341)
110 | NS-28 | Supply, installation, testing & Commissioning of Biometric finger print and card reader including all accessories complete in all respects. | 1 | No. | 3 | 0 | 0
111 | NS-29 | Supply, installation, testing & Commissioning of Exit push buttons. | 1 | No. | 3 | 0 | 0
112 | NS-30 | Supply, installation, testing & Commissioning of Electromagnetic Locks for Access Control System with necessary hardware as specified for centralized securtiy monitoring. - suitable for double door | 1 | Job | 3 | 0 | 0
113 | NS-31 | Supply, installation, testing & Commissioning of Heavy duty Auto Door Closer, Adjustable Hydraulic type Imported make | 1 | No. | 3 | 0 | 0
114 | NS-32 | Supply, installation, testing & Commissioning of Manual Emergency Override key Switch | 1 | No. | 3 | 0 | 0
115 | NS-33 | Separate machine as per the requirements of customized software/controller with following minimum specifications. Intel Desktop Board , CPU Core i5 2.0 Ghz 7th generation , Intel based graphics card , 8GB RAM ,SSD , Super Drive , Keyboard , Mouse , LED Screen , Operating System , Minimum 04 USB ports , 10/100/1000 Mbps LAN Card Along with Access Control Management Software with licenses for Server , Access Control System , Alarm Management , Operator Client , 2000 cards , required number of doors along with Security Control system features a password protected user logon system suitable to interface with CCTV and Fire Alarm/ BMS of the building including all licensing and security requirements. | 1 | Nos. | 1 | 0 | 0
UNINTERRUPTED POWER SUPPLY (UPS)
116 | NS-34 | Supply, installation, testing & commissioning of UPS System of rating 50 KVA three phase 400 V 50 Hz with standard back up time with lead acid batteries (VRLA) 05 years life, CD with Software, Network Management Card, power module UPS Cable Rs 232 Fabricated according to IP 51 for industrial environment complete in all respect as per technical specifications. | 1 | Job | 1 | 0 | 0
B4. |  | EXTERNAL DEVELOPMENT WORKS
TRANSFORMERS
(Ref. Specification Section-8001)
117 | NS-35 | Supply & Installation of Outdoor type 400 KVA, three phase, 11/0.415 kV Pole mounted transformer painted in dark grey color. The complete unit shall be designed, fabricated commissioned as per WAPDA's Latest technical specification with latest ammendments | 1 | Job | 1 | 0 | 0
LOW VOLTAGE D.G. SET
Ref. Spec. Sec. 8001, 8111, 8240.
118 | NS-36 | 200 kVA, Prime Rating 415 volt D.G. Set skid mounted including control / Instrument Panels, generator Panel, fuel day tank and all accessories along with Sound proof Canopy, locally manufactured for 200 kVA Prime D.G. Set. etc. complete in all respect including factory testing expenditure as mentioned in Clause 13 of Section 8001. | 1 | Job. | 1 | 0 | 0
119 | NS-37 | AMF/ATS panel commissioning of suitable free standing panel for 200 kVA D.G. Set consisting of all controls, mains failure sensing equipment MOR, 40 kA Class II SPDs, Phase Failure/Phase Rotation Relay, monitoring instruments, AMF/ATS Module Card, motorized changeover circuit breakers of suitable rating and rupturing capacity (contactor not acceptable), auto start/stop, auto synchronizing and auto load sharing system, suitable for 200 KVA generator set, internal wiring, all necessary accessories complete in all respects. In case of failure of WAPDA, ATS should have the provision of shifting the load manually. | 1 | Job. | 1 | 0 | 0
EARTHING SYSTEM
(Ref. Specification Section-8001, 8240)
120 | NS-38 | Earth Electrode for earthing shall comprise of 75 mm x 4877 mm x 6 mm thick copper plate with 4 Nos. 6 mm dia brass nuts, bolts and washers 70 sqmm HDHC Copper wire as earthing leads.
A 100 mm dia Medium Duty GI pipe shall be used with 10 mm dia holes @500 mm c-c. The total length of this GI pipe should be 45 ft.
A 150 mm dia 80 ft long hole should be drilled in ground by percussion method and above mentioned 100 mm dia medium duty GI pipe should be fixed in this hole simultaneously up to the depth of 60 ft from NSL.
When the drilling up to 80 ft depth is complete, The above mentioned earth electrode shall be drop down to the bottom of the hole with the help of 2 Nos 70 sqmm earth leads.
|  | Once the plate is in place fill in the hole with moisture retaining bentonite slurry with tremie method up to the top. When the bentonite settle down cast a (1:4:8) concrete manhole 700 mm x 700 mm & 500 mm deep as shown in the drawing. Place a medium duty CI cover as shown in the drawing. | 1 | Job | 8 | 0 | 0
Cost of Non-Scheduled Items (Rs.) | [6 empty] | 0
Total Cost of Scheduled Items & Non-Scheduled Items (Rs.) | [6 empty] | 0

## 3. Plumbing
UNHCR PAKISTAN
CONSTRUCTION OF CCU BLOCK AT DISTRICT HEADQUARTER HOSPITAL, BANNU
ENGINEER'S ESTIMATE
PLUMBING WORKS
ITEM NO. | KPK MRS 2022 REF. NO. / NS (2nd BI ANNUAL) | DESCRIPTION | UNIT | QTY | UNIT RATE (Rs.) | TOTAL AMOUNT (Rs.)
(a) | (b) | (c) | (d) | (e) | (f) | (g)
C1. |  | BUILDING PLUMBING WORKS
SCHEDULED ITEMS
SANITARY FIXTURES AND FITTINGS
1 | 14-03-a + 14-25-a + 14-78 +14-157 | Providing and fitting glazed earthenware White water closet (WC), squatter type (orisa pattern) combined with foot rest, including low level plastic flushing cistern 3 gallons (13.63 litres) capacity, P-Trap (uPVC), 1/2" CP tee stop-cock, complete in all respects. | Each | 11 | 0 | 0
2 | 14-01-a +14-02-b +14-10-a +14-25-a | Providing and Fixing glazed Earthen ware White WC European type of approved make/size with plastic double seat and cover , glazed earthenware White low down flushing cistern 3 gallons (13.63 Liters) capacity including bracket set, copper connection etc, 1/2" CP tee stop-cock, complete in all respects. | Each | 15 | 0 | 0
3 | 14-05-a-01 +14-25a +14-29-b +14-45-a | Providing & Fixing glazed earthen ware White wash hand basin (WHB) with pedestal (Best Quality) complete of size 22"x16" including bracket set, waste coupling, CP swan-neck double way cock ½"dia , 1/2" CP tee stop-cocks(02 Nos.), and CP bottle trough with waste pipe 1.25"(32mm) i/d, etc. complete in all respects. | Each | 18 | 0 | 0
4 | 14-06-b +14-27-a | Providing and Fixing stainless steel sink with drain board size 36"x 18" (Best Quality), including set of brackets, waste pipe etc including CP mixing valve for sink. (in kitchen) | Each | 1 | 0 | 0
5 | 14-159 + 14-25-a +14-29-b +14-45-a | Providing & Fixing Undercounter Vanity type wash hand basin of approved make, colour, size, shape and quality, including jointing and sealing material, CP swan-neck double way cock ½"dia , 1/2" CP tee stop-cocks, and CP bottle trough with waste pipe 1.25" dia etc. with all accessories for complete installation. | Each | 11 | 0 | 0
6 | 14-27-a +14-26-a | Providing and Fixing CP mixing valve for WHB, sink or shower of approved best quality with CP shower rose : 1/2"x4" (bath shower) | Each | 1 | 0 | 0
7 | 14-08-b +14-29-a | Providing and Fixing glazzed earthenware sink 25"x18" with chromium plated (CP) or brass oxidized swan neck cock 1/2" dia single way, including set of bracket set, waste pipe and waste coupling. | Each | 1 | 0 | 0
8 | 14-13 | Providing & Fixing CP soap dish. | Each | 24 | 0 | 0
9 | 14-15 | Providing & Fixing CP toilet paper holder. | Each | 9 | 0 | 0
10 | 14-16-a | Providing & Fixing CP towel rail complete: 24" long, 3/4" dia. | Each | 20 | 0 | 0
11 | 14-17-b | Providing and fixing best quality looking glass 5mm thick neatly fitted with bracket as per instruction of Engineer In-charge complete | Sft | 450 | 0 | 0
12 | 14-18-a | Providing & Fixing best quality 5mm glass shelf (60x13 cm) 24"x5" with chromium plated brackets & railing. | Each | 18 | 0 | 0
13 | 14-24-a | Providing & Fixing CP bib cock, heavy duty of approved quality: 2cm 3/4". | Each | 1 | 0 | 0
14 | 14-158 | Grab bar (ROCA make) with W.C of special person's toilet including all fittings with complete installation. | Each | 14 | 0 | 0
15 | 14-86 | Providing & fixing chromium plated double bib-cock with Muslim Shower of approved quality Complete is all respects | Each | 26 | 0 | 0
16 | 14-160-b | Electric water coolers of 40 gallons capacity including inlet and outlet connections, gate valve on inlet, electric connection upto power socket, and all other accessories for complete installation. | Each | 4 | 0 | 0
17 | 14-161 | Triple water filter (10") including inlet and outlet connections, power supply, and all accessories for complete installation | Each | 4 | 0 | 0 | 260000 | 0
18 | 23-05-a | Constructing gully grating chamber complete with CI gully trap, weighing 81 lbs. frame hinged. | Each | 8 | 0 | 0
19 | 15-220-b | Supply and fixing of 15-25 Litres Electric Geyser including all accessories and fittings | Each | 10 | 0 | 0
20 | 14-62-b | Providing and Fixing Normal quality gas water heaters 30 gallons capacity | Each | 5 | 0 | 0
WATER SUPPLY PIPES AND FITTINGS
21 |  | G.I. water pipes (cold and hot water, in ducts & in exposed condition) Conforming to BS-1387 (1985), Medium Grade, I/c all fittings, wrapping glass wool thermal insulation with aluminium vapour barrier, making holes in concrete or masonry and then repairing holes, supports and hangers etc. of approved make of the following diameters, complete in all respects:
| 14-162-a | 01 inch | Rft | 100 | 0 | 0
22 | 14-163-a | G.I. water pipes (in buried conditions) conforming to BS-1387, Medium Grade, I/c all fittings, wrapping polythene tape, giving anticorrosion treatment, applying protective painting, making holes in concrete or masonry and then repairing holes, flushing, disinfecting, testing and commissioning etc. of approved make, of the following diameters,complete in all respects. 3/4" (20 mm) Nominal Pipe Size (NPS) | Rft | 20 | 0 | 0
23 | 14-73-b | Providing of thermal insulation of high density (64kg/m3) fiber glass pipe insulation faced with aluminium foil for chilled/hot water piping complete: 3/4" dia | Rft | 20 | 0 | 0
24 |  | Providing, laying cutting, jointing, testing PPRC pipeline in walls/trenches with pipes (confirming to DIN 8077/8078, PN 20 of approved quality & fittings conforming to DIN 16962,PN25 of the same manufacturer) for cold/hot water supply systems including specials complete in all respect as per specifications:
| 14-35-g | 1/2" i/d (25mm o/d) | Rft | 360 | 0 | 0
| 14-35-a | 3/4" i/d (32mm o/d) | Rft | 300 | 0 | 0
| 14-35-b | 1" i/d (40mm o/d) | Rft | 100 | 0 | 0
SOIL, WASTE, VENT AND STORM DRAINAGE PIPES
25 |  | Supplying and Fixing UPVC soil waste and vent pipe class B of following diameter for sanitary drainage:
| 14-144-a | 6" dia | Rft | 10 | 0 | 0
| 14-144-b | 4" dia | Rft | 500 | 0 | 0
| 14-144-c | 3" dia | Rft | 400 | 0 | 0
26 |  | Supplying and Fixing UPVC soil waste and vent pipe class B of following diameter for storm drainage:
| 14-144-b | 4" dia | Rft | 150 | 0 | 0
| 14-144-c | 3" dia | Rft | 10 | 0 | 0
27 |  | uPVC Soil, Waste and vent pipes conforming to ISO:3633 type "B" or BS-4514/5255 class "A" ,including imported rubber ring/solvent cement fittings, jointing, cutting, and breaking concrete/masonry and then making it good, applying painting, cleaning and testing etc. complete in all respects.(for sanitary drainage)
| 14-144-d | 2" dia | Rft | 150 | 0 | 0
| 14-144-e | 1-1/2" dia | Rft | 10 | 0 | 0
28 | 14-164 | uPVC Multi Floor Trap (110x75mm) including strainer; supports; making required number of connections; breaking concrete or masonry work & then making it good; etc. | Each | 21 | 0 | 0
29 |  | uPVC floor Cleanout including 2 No. 45o elbows, transition pipe, SS screwed plug/cover assembly jointed air-tight with pipe, breaking concrete or masonry work & then making it good, etc complete in all respects
| 14-165-a | (i) 3" dia | Each | 1 | 0 | 0
| 14-165-b | (ii) 4" dia | Each | 1 | 0 | 0
0
30 | 14-170 | Cowel on vent pipes of the following diameter. (i) 3" | Each | 15 | 0 | 0
VALVES
31 |  | Providing & Fixing gun metal peet/gate valve (screwed) of following diameters:
| 14-28-f | 3/4" dia | Each | 10 | 0 | 0
| 14-28-g | 1 inch. | Each | 8 | 0 | 0
32 | 14-169 | Air relief valves, of approved make (Italy or equivalent), including jointing arrangement with pipe; nuts, bolts etc. complete in all respects.
|  | (i) 3/4 " | Each | 5 | 0 | 0
33 | 14-168 | Brass/Bronze swing type check valves on water supply pipes, conforming to BS standards, including jointing arrangement of pipes on both ends of valves; nuts, bolts etc. complete in all respects, of following internal diameters. 1-1/4 " | Each | 4 | 0 | 0
FIRE FIGHTING
34 | 14-146 | Fire Hose cabinet with 30 meter Hose Reel and Nozzle Complete with accessories | Each | 2 | 0 | 0
35 | 14-172-a | Supplying and fixing of Dry Chemical Powder Fire Extinguisher 6Kg Capacity complete in all respect | Each | 4 | 0 | 0
36 | 14-172-b | Supplying and fixing of Foam Type fire extinguishers capacity 12 liters complete in all respect | Each | 4 | 0 | 0
C2. |  | EXTERNAL PLUMBING WORKS
WATER SUPPLY NETWORK
37 | 03-51 | Excavation of trench in all kinds of soils except cutting in rock for pipelines upto 1.5m depth | 1000 Cft | 1500 | 0 | 0
38 | 03-67-c | Structural backfill using Common Material available at site. | 1000 Cft | 945 | 0 | 0
39 | 07-30 | Supplying and filling sand under floor or plugging in wells | 100 Cft | 450 | 0 | 0
40 |  | Providing, laying, cutting, jointing, testing and disinfecting High Density Polyethylene Pipe (HDPE) Din-8074/Din-8075/ISO-4427 in trenches, complete in all respects PN-12.5
| 24-30-c-04 | (40 mm dia) | Rft. | 100 | 0 | 0
| 24-30-c-05 | (50 mm dia) | Rft. | 100 | 0 | 0
| 24-30-c-06 | (63 mm dia) | Rft. | 100 | 0 | 0
FIREFIGHTING NETWORK
41 | 03-51 | Excavation of trench in all kinds of soils except cutting in rock for pipelines upto 1.5m depth | 1000 Cft | 2800 | 0 | 0
42 | 03-67-c | Structural backfill using Common Material available at site. | 1000 Cft | 1890 | 0 | 0
43 | 07-30 | Supplying and filling sand under floor or plugging in wells | 100 Cft | 880 | 0 | 0
44 | 24-22-c | Providing and fixing sluice valve of BSS quality (BS 5163) and weight Class 'B' for GI & PVC pipeline (including cost of jointing material):- c) 6" (150 mm) dia of Valve | Each | 2 | 0 | 0
45 | 24-23 | Providing and Fixing fire hydrants BSS quality and weight of of 2-1/2" (65 mm) (including cost of jointing material) | Each | 2 | 0 | 0
46 |  | Providing, laying, cutting, jointing, testing and disinfecting High Density Polyethylene Pipe (HDPE) Din-8074/Din-8075/ISO-4427 in trenches, complete in all respects except excavation. PN-16
| 24-30-d-09 | (110 mm dia) | Rft. | 300 | 0 | 0
.
| 24-30-d-10 | (160 mm dia) | Rft. | 50 | 0 | 0
VALVE CHAMBER FOR FIREFIGHTING SYSTEM
47 | 03-49-a | Excavation in open cut for sewers & manhole except shingle, gravel & rock : Upto 2m | 1000 Cft | 210 | 0 | 0
48 | 06-05-h | Plain Cement Concrete incl. placing, compacting, finishing & curing (Ratio 1:3:6) | 100 Cft | 10 | 0 | 0
49 | 06-05-i | Plain Cement Concrete incl. placing, compacting, finishing & curing (Ratio 1:4:8) | 100 Cft | 10 | 0 | 0
50 | 06-07-a-03 | RCC in roof slab, beam, column & other structural members, insitu or precast. Type C (1:2:4) | 100 Cft | 95 | 0 | 0
51 | 06-07-b-03 | RCC in raft foundation slab, base slab of column & ret. wall etc, not including in 06-06. Type C(1:2:4) | 100 Cft | 20 | 0 | 0
52 | 06-08-c | Supply & fabricate M.S. reinforcement for cement concrete (Hot rolled deformed bars Grade 40) | 100 Kg | 255 | 0 | 0
53 | 06-47-a | Erection and removal of Form work with Steel Surface Finishing for RCC or Plain Concrete in any shape - Position / Horizontal | 100 Sft. | 150 | 0 | 0
54 | 06-47-b | Erection and removal of Form work with Steel Surface Finishing for RCC or Plain cement Concrete in any shape - Position / Vertical | 100 Sft. | 240 | 0 | 0
SEWERAGE NETWORK
55 | 03-49-a | Excavation in open cut for sewers & manhole except shingle, gravel & rock : Upto 2m | 1000 Cft | 10000 | 0 | 0
56 | 03-49-b | Excavation in open cut for sewers & manhole except shingle, gravel & rock : 2m to 5m | 1000 Cft | 1000 | 0 | 0
57 | 03-67-c | Structural backfill using Common Material available at site. | 1000 Cft | 7875 | 0 | 0
58 | 06-05-f | Plain Cement Concrete including placing, compacting, finishing and curing ( Ratio 1:2:4) | 100 Cft | 10 | 0 | 0
59 | 7-30 | Supplying and filling sand under floor or plugging in wells | 100 Cft | 2100 | 0 | 0
RCC MANHOLES
60 | 03-49-a | Excavation in open cut for sewers & manhole except shingle, gravel & rock : Upto 2m | 1000 Cft | 1500 | 0 | 0
61 | 03-49-b | Excavation in open cut for sewers & manhole except shingle, gravel & rock : 2m to 5m | 1000 Cft | 300 | 0 | 0
62 | 03-67-c | Structural backfill using Common Material available at site. | 1000 Cft | 100 | 0 | 0
63 | 06-05-h | Plain Cement Concrete incl. placing, compacting, finishing & curing (Ratio 1:3:6) | 100 Cft | 30 | 0 | 0
64 | 06-05-i | Plain Cement Concrete incl. placing, compacting, finishing & curing (Ratio 1:4:8) | 100 Cft | 50 | 0 | 0
65 | 06-07-a-03 | RCC in roof slab, beam, column & other structural members, insitu or precast. Type C (1:2:4) | 100 Cft | 800 | 0 | 0
66 | 06-07-b-03 | RCC in raft foundation slab, base slab of column & ret. wall etc, not including in 06-06. Type C(1:2:4) | 100 Cft | 70 | 0 | 0
67 | 06-08-c | Supply & fabricate M.S. reinforcement for cement concrete (Hot rolled deformed bars Grade 40) | 100 Kg | 1950 | 0 | 0
68 | 14-37-c | Supply and Fixing CI manhole cover with frame etc complete 24" dia | Each | 15 | 0 | 0
69 | 06-47-a | Erection and removal of Form work with Steel Surface Finishing for RCC or Plain Concrete in any shape - Position / Horizontal | 100 Sft. | 400 | 0 | 0
70 | 06-47-b | Erection and removal of Form work with Steel Surface Finishing for RCC or Plain cement Concrete in any shape - Position / Vertical | 100 Sft. | 500 | 0 | 0
71 | 14-155 | Galvanised MS ladder rings 3/4" dia inside and outside water tanks; Each rung of 12" width, 6" projected outside the wall and 6" embeded in RCC on both ends; including all necessary works for complete installation | kg | 50 | 0 | 0
0
Cost of Building Plumbing works Scheduled Items (Rs.) | [5 empty] | 0
Add Area factor on KP MRS-2022 (2nd Bi Annual) for District Bannu @ 3% (Rs.) | [5 empty] | 0
Total Cost of Building Plumbing works Scheduled Items (Rs.) | [5 empty] | 0
NON-SCHEDULED ITEMS
C3. |  | BUILDING WORKS
GENERAL NOTE
Supply, installation, testing and commissioning of the following items of work, including all labour, tools, plant, accessories, etc. required for completion of each item as per specifications and as approved by the Engineer.
SANITARY FIXTURES AND FITTINGS
(Ref. Specification Section-5100)
72 | NS-01 | CP Small hook of any size and shape, of approved make, with plugs and screws, fixed to concrete, brick, stone or wood work, complete in all respects. | Each | 52 | 0 | 0
73 | NS-02 | Electric Hand Dryer (automatic) with easy to mount kit, of approved make & model and all required accessories for complete installation. | Each | 7 | 0 | 0
74 | NS-03 | CP long lever mixer for hot and cold water to be installed at scrubs of approved make, with accessories., fixed to concrete, brick, stone or wood work, complete in all respects . | Each | 4 | 0 | 0
WATER SUPPLY PIPES AND FITTINGS
(Ref. Specification Section-5100)
75 | NS-04 | Providing and fixing GI (28swg) cladding on hot and cold water supply pipe on roof with thermal insulation including all required accessories complete for following pipe diameters
| (a) | 3/4" dia | Rft | 20 | 0 | 0
| (b) | 1" dia | Rft | 100 | 0 | 0
SOIL, WASTE AND VENT PIPES & FITTINGS
(Ref. Specification Section-5100)
76 | NS-05 | 3"dia uPVC Floor Trap with Stainless Steel-304 Top Tile strainer; supports; making required number of connections; breaking concrete or masonry work & then making it good; etc. | Each | 14 | 0 | 0
RAIN WATER DRAINAGE PIPES AND FITTINGS
(Ref. Specification Section-5100)
77 | NS-06 | Supply & installation of C.I. roof drain of following diameters, including strainer, flushing material, and all accessories for complete installation, as per specifications.
| (a) | 03 inches | Each | 1 | 0 | 0
| (b) | 04 inches | Each | 4 | 0 | 0
FIRE FIGHTING
(Ref. Specification Section-5216)
78 | NS-07 | MS pipes with specials and clamps etc, conforming to ASTM A53 Sch. 40, including fixing, cutting, welding, fixing & support systems; and other fittings complete with and including the cost of breaking, through walls and slabs, making walls & slabs good thereafter, etc, painting with two coats of approved enamel paint after cleaning the pipe.
| (a) | 1.5 inches | Rft | 20 | 0 | 0
| (b) | 2 inches | Rft | 50 | 0 | 0
| (c) | 3 inches | Rft | 50 | 0 | 0
79 | NS-08 | Pressure reducing arrangement consisting of pressure reducing valve (PRV) and gate valves (3 Nos.), pressure gauge, unions etc.; on pipes of following nominal sizes including jointing arrangement etc. complete in all respects as per standards, manufacturer's recommendations, and as directed by the Engineer.
|  | 1-1/2 inches | Each | 2 | 0 | 0
C4. |  | EXTERNAL FIREFIGHTING WORKS
(Ref. Spec: 5150, 5216, 5220)
80 | NS-09 | Cast Iron manhole cover & frame conforming to BS-497 including coats of Red oxide/ enamel paint, on chambers/manholes including all fittings for complete installation.
| (a) | 36" x 36" (90 Kg) | Each | 2 | 0 | 0
81 | NS-10 | Steel fire hose cabinet with floor mounting stand and foundation to fix it 2'-6" above ground level, including 100feet long fire hose (2-1/2" dia), with dia 2-1/2" male female brass coupling & jet nozzle etc.complete in all respects as shown in drawing or as directed by the Engineer. | Each | 2 | 0 | 0
SEWERAGE NETWORK
(Ref. Specification Section-5100)
82 | NS-11 | uPVC non-pressure pipes for sanitary drainage conforming to BS-5481/BS-4660/EN1401 (SN8) with rubber ring fittings and specials compatible with pipe material as per manufacturer's recommendations, complete in all respects, flushing cleaning and disinfecting as per specifications and as directed by the Engineer of following diameters:
| (a) | 250 mm | Rft | 500 | 0 | 0
Cost of Non-Scheduled Items (Rs.) | [5 empty] | 0
Total Cost of Scheduled Items & Non-Scheduled Items (Rs.) | [5 empty] | 0

## 4. MGPS
UNHCR PAKISTAN
CONSTRUCTION OF CCU BLOCK AT DISTRICT HEADQUARTER HOSPITAL, BANNU
ENGINEER'S ESTIMATE
MEDICAL GAS PIPING WORKS
ITEM NO. | KPK MRS 2022 REF. NO. / NS (2nd BI ANNUAL) | DESCRIPTION | UNIT | QTY | UNIT RATE (Rs.) | TOTAL AMOUNT (Rs.)
(a) | (b) | (c) | (d) | (e) | (f) | (g)
D1. |  | NON-SCHEDULED ITEMS
M. MECHANICAL WORKS
Ref. Specification No. 8467 & 9000
1 | M-NS-01 | Copper Pipes
Supply, installation testing and commissioning of medical grade copper pipe Type " L " conforming to BS EN 13348:2001 for medical gas supply network with all fittings, valves and supports including painting in approved shade complete as per specifications and drawings of following diameters:-
|  | a) 42 mm Dia. | R.ft. | 20 | 0 | 0
|  | b) 35 mm Dia. | R.ft. | 30 | 0 | 0
|  | c) 28 mm Dia. | R.ft. | 200 | 0 | 0
|  | d) 22 mm Dia. | R.ft. | 300 | 0 | 0
|  | e) 15 mm Dia. | R.ft. | 700 | 0 | 0
|  | f) 12 mm Dia. | R.ft. | 3750 | 0 | 0
2 | M-NS-02 | OXYGEN MANIFOLD
Supply, installation, testing and commissioning of Oxygen (O2) Gas Manifold System for (5 x 2) Cylinders Installation comprising primary header, secondary header, 2 cylinder rack, Non-return valve, blanking ring and corner connector along with flexible copper tailpipes to connect the gas cylinders to the header assemblies complete with all fittings and accessories and as per specifications and drawings. the manifold shall comply with HTM02-01, NHS Code C11, with M.S railing minimum height 1525 mm around cylinder manifold along with access door at location mentioned below:
|  | a) For 5 x 2 cylinders installation | Nos. | 1 | 0 | 0
3 | M-NS-03 | NITROUS OXIDE MANIFOLD
Supply, installation, testing and commissioning of Nitrous Oxide (N2O) Gas Manifold System for (5 x 2) Cylinders Installation comprising primary header, secondary header, 2 cylinder rack, Non-return valve, blanking ring and corner connector along with flexible copper tailpipes to connect the gas cylinders to the header assemblies complete with all fittings and accessories and as per specifications and drawings. the manifold shall comply with HTM02-01, NHS Code C11, with M.S railing minimum height 1525 mm around cylinder manifold along with access door at location mentioned below:
|  | a) For 5 x 2 cylinders installation | Nos. | 1 | 0 | 0
4 | M-NS-04 | Medical Air Manifold
Supply, installation, testing and commissioning of Automatic Medical Air Manifold System for (5 x 2) Cylinders Installation comprising primary header, secondary header, 2 cylinder rack, Non-return valve, blanking ring and corner connector along with flexible copper tailpipes to connect the gas cylinders to the header assemblies complete with all fittings and accessories and as per specifications and drawings. the manifold shall comply with HTM 02-01, NHS Code C11, with M.S railing minimum height 1525 mm around cylinder manifold along with access door at location mentioned below:
|  | a) Gas Cylinder Room | Nos. | 1 | 0 | 0
5 | M-NS-05 | Area Valve Service Unit
Supply, installation, testing and commissioning of Area Valve Service Unit (AVSU) conforming to BS EN 737-3, HTM02-01, NHS Code C11 and NIST connections to BS EN 739 able to accept 22mm pipe entry from side, top, bottom or rear and as per specifications and drawings at location indicated on drawing and for handling number of gases as mentioned below:
|  | a) Two Gases | Nos. | 5 | 0 | 0
|  | b) Six Gases | Nos. | 1 | 0 | 0
6 | M-NS-06 | Local Area Alarm Panel
Supply, installation, testing and commissioning of medical gas Local Area Alarm Panel (LAAP) conforming to HTM02-01/C11 able to monitoring 6 medical gas services by means of pressure sensor, cover and back box shall be stove enameled conforming to BS 4800:12B15, equipped with LED's display and an audible warning facility with mute selection and able to automatically reset when the gas service returns to normal, complete with all fittings and as per specification and drawings and for handling number of gases as mentioned below:
|  | a) Two Gases | Nos. | 5 | 0 | 0
|  | b) Six Gases | Nos. | 1 | 0 | 0
PLANT & EQUIPMENT
7 | M-NS-07 | Combined Medical Air Plant (MA-4) & Surgical Air Plant (SA-7)
Supply, installation, testing and commissioning of oil less duplex Combined Type Medical & Surgical Air Plant with duplex regulating set (7 bar to 4 bar). The plant shall consist of duplex compressor (each compressor shall be sized to provide the system's full design flow), receiver, duplex filter and dryer conforming to HTM02-01/C11. The air compressor shall be of proven reliability and shall be driven by electric motors to class F insulation and noise levels tested to BS 4999. The recover shall conform to EN 286 or BS 5169/1975 Class 3 Grand E or better complete with all accessories and fittings and as per specification and drawings at location marked on drawing and capable of providing a combined net flow rate of compressed air as mentioned below:
|  | a) Flow Rate 2000 L/min | Nos. | 1 | 0 | 0
8 | M-NS-08 | Anesthetic Gas Scavenging System (AGSS)
Supply, installation, testing and commissioning of AGSS plant for a constant flow rate between a maximum of 50 liters / min with 1 kPa resistance to flow and a minimum of 25 liters/min with 2 kPa resistance to flow at each terminal unit, irrespective of the number of terminal units in use, conforming to BSEN 737-2 (1998) for disposal systems complete with all accessories and fittings and as per specification and drawings at location mentioned below:
|  | a) Medical Gas Plant Room | Nos. | 1 | 0 | 0
9 | M-NS-09 | Multi movement Pendants
Supply, installation, testing and commissioning of Multi movement Pendants with electromagnetic break system able to mount up to 14 medical gases and four vacuum Terminal Units and 2 twin & 2 single (minimum) electric sockets / devices conforming to BS EN 793. Medical gas / vacuum services shall be arranged in accordance with HTM02-01/C11, complete with all fittings and as per specifications and drawings at location mentioned below:
|  | a) O.T. | Nos. | 1 | 0 | 0
10 | M-NS-10 | Wall Mounted Terminal Units
Supply, installation, testing and commissioning of Wall Mounted Terminal Units, suitable for surface or flush mounting, for supply of medical gases complying with ISO 9170, BS EN 737-1"1998 (BS 5682: 1998 for probes), HTM02-01 and C11 complete with all accessories and fittings and as per specification and drawings and at locations indicated on drawing for supply of following type of gases:
|  | a) Oxygen Outlets | Nos. | 45 | 0 | 0
|  | b) MA-4 Outlets | Nos. | 45 | 0 | 0
11 | M-NS-11 | Line Ball Valves
Supply, installation, testing and commissioning of non-lubricated type Ball Valve suitable for medical gas use, with copper pipe stubs, nickel plated brass body, hard chrome plated brass ball and in compliance with HTM02-01 complete in all respect and as per specification and drawing having following diameters:
|  | a) 28 mm Dia. | Nos. | 2 | 0 | 0
|  | b) 22 mm Dia. | Nos. | 2 | 0 | 0
|  | c) 15 mm Dia. | Nos. | 1 | 0 | 0
|  | d) 12 mm Dia. | Nos. | 1 | 0 | 0
Total Cost of Medical Gas Piping Works Non-Scheduled Items (Rs.) | [5 empty] | 0

## All Block (hidden)
D H Q HOSPITAL BANNU OPD / ADMIN BLOCK
MEASUREMENT SHEET
S.NO | Description | NO | L | B | H | QTY | UNIT
GROUND FLOOR
Earth work
C-01 | Earth fill in lawns | 1 | 100 |  |  | 100 | Cft
C-02 | Earth Under Floor | 1 | 12323 | 0.5 | 0.25 | 1540.375 | Cft
C-03 | Extra lead 15 m | 1 | 15546 |  |  | 15546 | Cft
C-04 | Transportation 250 to 500m. | 1 | 15546 |  |  | 15548 | Cft
C-05 | Transportation 500m to 1.5 km | 1 | 15546 |  |  | 15546 | Cft
C-06 | Transportation 1.5 km to 8.0 km. | 1 | 15546 |  |  | 15546 | Cft
C-07 | Transportation beyond of 8.0 km. | 1 | 15546 |  |  | 15546 | Cft
| Excavation in Foundation Ordinary Soil |  | 12323 |  |  | 12323
| Excavation in Comon Material |  | 12323 |  |  | 12323
| Backfill using granular material |  | 100 |  |  | 100
| Dismantling brick work in lime or cement mortar |  | 100 |  |  | 100
| Dismantling cement block masonry |  | 100 |  |  | 100
| Dismantling : Plain Cement Concrete 1:4:8 |  | 100 |  |  | 100
| Dismantling : Plain Cement Concrete 1:3:6 |  | 10831 |  |  | 10831
| Dismantling : Plain Cement Concrete 1:2:4 |  | 100 |  |  | 100
| Dismantling RCC, separating reinforcement, cleaning & straightening the same |  |  |  |  | 100
| Scraping : Ordinary distemper, oil bound distemper or paint off wall (also on roof) |  |  |  |  | 41653
| Total Transportation |  |  |  |  | 77730 | Cft
| Transportation in five component |  |  |  |  | 15546 | Cft
C-08 | Excavation in Foundation Ordinary Soil | 1 | 12323 |  |  | 12323 | Cft
C-09 | Excavation in Comon Material | 1 | 12323 |  |  | 12323 | Cft
C-10 | Backfill using granular material | 1 | 100 |  |  | 100 | Cft
Dismantling ( Demolishing)
C-11 | Brick Work | 1 | 100 |  |  | 100 | Cft
C-12 | Block Masonary | 1 | 100 |  |  | 100 | Cft
C-13 | PCC 1:4:8 | 1 | 100 |  |  | 100 | Cft
C-14 | PCC 1:3:6 | 1 | 10831 |  |  | 10831 | Cft
C-15 | PCC 1:2:4 | 1 | 100 |  |  | 100 | Cft
C-16 | RCC Seprating Reinfocement Cleaning & Straightening | 1 | 100 |  |  | 100 | Cft
C-17 | Scraping Ordinary distemper, Oil Bound distemper | 1 | 41653 |  |  | 41653 | Sft
C-18 | Stone Ballast
| Stone Ballast undr pcc | 1 | 10831 |  |  | 10831
|  |  |  | Total Qty |  | 10831 | Cft
C-19 | P.C.C Under plinth
| P C C Class D | 1 | 10831 |  |  | 10831
|  |  |  | Total Qty |  | 10831 | Cft
C-20 | PCC 1:4:8 | 1 | 470 |  |  | 470 | Cft
C-21 | RCC 1:2:4 | 1 | 1175 |  |  | 1175 | Cft
C-22 | Steel G-40 | 1 | 4265 |  |  | 4265 | KG
C-23 | Aluminium sheet for Expansion Joint | 1 | 2100 |  |  | 2100 | Sft
C-24 | Aluminium sheet for Expansion Joint | 1 | 2100 |  |  | 2100 | Sft
C-25 | Form Work Horizontal | 1 | 3024 |  |  | 3024 | Sft
C-26 | Form Work Vertical | 1 | 6048 |  |  | 6048 | Sft
C-27 | G.FLOOR BRICK WORK
4.5" Brick WORK
| G.Floor | 1 | 1640 |  |  | 1640
|  |  |  | Total Qty |  | 1640 | Cft
C-28 | Brick Work First Floor | 1 | 2800 |  |  | 2800 | Cft
C-29 | Brick Work 2nd Floor | 1 | 50 |  |  | 50 | Cft
C-30 | Hollow Block 4" | 1 | 210 |  |  | 210 | Cft
C-31 | Hollow Block 8" | 1 | 241 |  |  | 241 | Cft
C-32 | Solid Block 4" | 1 | 210 |  |  | 210 | Cft
C-33 | Solid Block 8" | 1 | 241 |  |  | 241 | Cft
C-34 | Khura on Roof | 1 | 8 |  |  | 8 | Each
C-35
C-36 | Grouting 4.5" | 1 | 310 |  |  | 310 | Cft
C-37 | P.C.C Coloured Tile for Plinth Protection
| Plinth.P Area | 1 | 10033 |  |  | 10033
|  |  |  | Total Qty |  | 10033 | Sft
C-38 | Terrazo Tile Flooring
|  | 1 | 3500 |  |  | 3500
|  |  |  | Total Qty |  | 3500 | Sft
C-39 | Mosaic Marble Chips | 1 | 3133 |  |  | 3133
C-40 | Landing | 1 | 175 |  |  | 175
|  |  |  | Total Qty |  | 175 | Sft
C-41 | Tread | 1 | 642 | 1 |  | 642
|  |  |  | Total Qty |  | 642 | Sft
C-42 | 3/4" Thick Counter Marble/ Granite
| Recipition Counter Top | 1 | 2469 |  |  | 2469
|  |  |  | Total Qty |  | 2469 | Sft
C-43 | 3/4" Thick Counter Marble / Granite
|  | 1 | 2469 |  |  | 2469 | Sft
C-44 | 3/4" Thick Counter/Vanity Marble
| Toilet counter | 1 | 1373 |  |  | 1373
|  |  |  | Total Qty |  | 1373 | Sft
C-45 | 3/4" Thick Counter Marble
G.F
Kitchen Counter
| " | 1 | 440 |  |  | 440
|  |  |  | Total Qty |  | 440 | Sft
C-46 | Mosaic Dado Skirting Elevated water Tank Walls | 1 | 7500 |  |  | 7500 | Sft
C-47 | Marble Dado / Skirting | 1 | 109 |  |  | 109 | Sft
C-48 | Ramp Flooring Vinyle Tile
Main Ramp
Entrance
|  | 1 | 3175 |  |  | 3175
|  |  |  | Total Qty |  | 3175 | Sft
C-49 | Pocelain ( Floor Tile ) 16"x 16"
|  | 1 | 5931 |  |  | 5931 | Sft
C-50 | Porcelain Tile Dado up to 4' Height and Floor
|  | 1 | 59915 |  |  | 59915 | Sft
C-51 | Granite Tile flooring
| Recipition Counter wall | 1 | 787 |  |  | 787 | Sft
C-52 | Chemical Polishig of Marble Dado | 1 | 109 |  |  | 109 | Sft
C-53 | 1/2" Thick internal plaster up to 20' height
|  | 1 | 116038 |  |  | 116038 | Sft
C-54 | Cement Plaster 20' to 30' 1/2" | 1 | 22806 |  |  | 22806
C-55 | Cement Plaster 20' heigh 3/4" | 1 | 55040 |  |  | 55040 | Sft
C-56 | Cement Plaster 20' to 30' 3/4" | 1 | 13170 |  |  | 13170 | Sft
C-57 | 3/8" Thick Under Soffit / Ceiling Plaster
|  | 1 | 1816 |  |  | 1816
|  |  |  | Total Qty |  | 1816 | Sft
C-58 | 3/8" Thick Under Soffit / Ceiling Plaster
|  | 1 | 1933 |  |  | 1933 | Sft
C-59 | Prime Coat of Chalk Under Distemper | 1 | 35385 |  |  | 35385 | Sft
C-60 | Wall Putty | 1 | 35385 |  |  | 35385 | Sft
C-61 | Distemper Paint New Surface
|  | 1 | 35385 |  |  | 35385 | Sft
C-62 | Distemper Paint Old Surface
|  | 1 | 41653 |  |  | 41653 | Sft
|  |  |  | Total Qty |  | 41653
C-63 | Grooved Cement Sand Plaster over Roughened plaster | 1 | 55040 |  |  | 55040 | Sft
C-64 | Grooved Cement Sand Plaster over Roughened plaster | 1 | 13710 |  |  | 13710 | Sft
C-65 | Expanded Metal
| Cement Plaster Qty | 1 | 27554 |  |  | 27554
|  |  |  | Total |  | 27554
|  |  |  | Total Qty |  | 27554 | Sft
C-66 | Door Closer
| DW-1 | 165 |  |  |  | 165
|  |  |  | Total Qty |  | 165 | NO'S
C-67 | Rim Lock
| G.Floor | 165 |  |  |  | 165
|  |  |  | Total Qty |  | 165 | NO'S
C-68 | Mineral Fiber Ceiling | 1 | 100 |  |  | 100
C-69 | Wooden Pannel Door SL
|  | 1 | 5336 |  |  | 5336
|  |  |  | Total Qty |  | 5336 | Sft
C-70 | Kick Plate
|  | 671 |  |  |  | 671
|  |  |  | Total Qty |  | 671 | Rft
C-71 | Aluminum fixed Window
|  | 1 | 851 |  |  | 851
C-72 | Aluminum Sliding Window
G. FLOOR
| W-2 | 1 | 7336 |  |  | 7336 | Sft
|  |  |  | Total Qty |  | 7336 | Sft
C-73 | Aluminum Window Fly screen
| W-2 | 1 | 3668 |  |  | 3668
|  |  |  | Total Qty |  | 3668 | Sft
0
C-74 | Aluminum Door DL
G. FLOOR
|  | 1 | 1380 |  |  | 1380
|  |  |  | Total Qty |  | 1380 | Sft
C-75 | Floor mounted Cabinet in Kitchen
| Kitchen | 1 | 108 |  |  | 108
|  |  |  | Total |  | 108
|  |  |  | Total Qty |  | 108 | Sft
C-76 | Wall Cabinet in Kitchen
| Kitchen | 1 | 72 | 1 |  | 72
|  |  |  | Total Qty |  | 72 | Sft
C-77 | UPVC Door
|  | 1 | 2419 |  |  | 2419
|  |  |  | Total Qty |  | 2419 | Sft
C-78 | Door Paint / polish
G.FLOOR
D-1
D-6
|  | 1 | 10673 |  |  | 10673
|  |  |  | Total Qty |  | 10674 | Sft
C-79 | Emulsion Paint First Coat
|  | 1 | 117698 |  |  | 117698
C-80 | Emulsion Paint 2nd Coat | 1 | 235396 |  |  | 235396
C-81 | Weather Shield 1ST First Coat | 1 | 67313 |  |  | 67313
C82 | Weather Shield 1ST 2nd Coat | 1 | 67313 |  |  | 67313
C-83 | Weather Shield 1ST 3rd Coat | 1 | 67313 |  |  | 67313
C-84 | Heavy Steel Work | 1 | 8 |  |  | 80
C-85 | Trusses, Staging of water tanks | 1 | 8 |  |  | 8
|  |  |  | Total Qty |  | 8 | Rft
C-86 | Collapsible gate
| W-2 | 1 | 80 |  |  | 80
|  |  |  | Total |  | 80
|  |  |  | Total Qty |  | 80 | Sft
C-87 | SS Railing
|  | 1 | 936 |  |  | 936
C-88 | MS Grill | 1 | 9910 |  |  | 9910
C-89 | Steel Door
|  | 1 | 120 |  |  | 120
0
|  |  |  | Total |  | 120
|  |  |  | Total Qty |  | 120 | Sft
C-90 | Cleaning of Water Tank | 1 | 55000 |  |  | 55000 | Per Gallon
C-91 | Termite Treatment
|  | 1 | 8565 |  |  | 8565
C-92 | Steel Nails
|  | 1 | 11790 |  |  | 11790
Dismantaling of floor & Wall Tile
Sft
C-93 | Dismantling / Disposal Wall tiles
|  | 1 | 162147 |  |  | 162147 | Sft
C-94 | Dismantling / Disposal / Plinth Protection
|  | 1 | 11789 |  |  | 11789
C-95 | Dismantling / removal Roof Treatment
|  | 1 | 67537 |  |  | 67537
C-96 | Dismantling / Stacking of Reinforcement | 1 | 100 |  |  | 100
C-97 | Dismantling of RCC Concrete
|  | 1 | 100 |  |  | 100
C-98 | Removal of Plaster
|  | 1 | 138844 |  |  | 138844
C-99 | Removal and Stacking False Ceiling incl Lead And Lift
|  | 1 | 61440 |  |  | 61440
C-100 | Removal and Stacking Of any type of Door / Window/ vent/ Skylight/Grill including rcc element and masonary work incl lesd and lift | 1 | 17322 |  |  | 17322
C-101 | Dismantling of Conduit on Surface | 1 | 3590 |  |  | 3590
C-102 | Dismantling of Conduit Recessed in Wall | 1 | 21540 |  |  | 21540
C-103 | Dismantling of WC'S Asian
|  | 1 | 270 |  |  | 270
C-104 | Dismantling of WC'S European
|  | 1 | 2160 |  |  | 2160
C-105 | Creating Holes in Slabs
|  | 1 | 9 |  |  | 9
C-106 | Providing and laying 1:3:6 Concrete in Sub Column on any floor | 1 | 1000 |  |  | 1000
C-107 | Water Proofing Membrane
|  | 1 | 67537 |  |  | 67537
C-108 | Plan G.i Sheet
|  | 1 | 135074 |  |  | 135074
C-109 | Plan G.i Sheet
|  | 1 | 1150 |  |  | 1150
C-110 | Porcelain (Wall tile) 16" x 16"
|  | 1 | 24629 |  |  | 24629
|  |  |  | Total Qty |  | 24629 | Sft
C-111 | Porcelain Tile Flooring
|  | 1 | 59915 |  |  | 59915
|  |  |  | Total Qty |  | 59915 | Sft
#REF!
C-112 | Marble Riser / dado / skirting
|  | 1 | 363 |  |  | 363
C-113 | 3/4" Granite Red Rubi
|  | 1 | 400 |  |  | 400
Epoxy flooring
C-114
| X-RAY | 1 | 2765 |  |  | 2765
|  |  |  | Total |  | 2765
|  |  |  | Total Qty |  | 2765
C-115 | Epoxy Painting
|  | 1 | 3337 |  |  | 3337 | Sft
C-116 | Matt Enamel / Antibacterial Paint Inner Walls
|  | 1 | 124946 |  |  | 124946
|  |  |  | Total Qty |  | 124946 | Sft
C-117 | X-RAY Room Wall
| Lead Lining 3/4" overlaid by laminated sheet board | 1 | 70 |  | 11.5 | 805
|  |  |  | Total |  | 805
|  |  |  | add 5% |  | 40.25
|  |  |  | Total Qty |  | 845.25 | Sft
C-118 | Lead Lining
|  | 1 | 150 |  |  | 150
C-119 | Dry Partition
|  | 1 | 400 |  |  | 400
C-120 | 12mm Temperd glass
|  | 1 | 150 |  |  | 150
C-121 | FRD
|  | 1 | 2 |  |  | 2
C-122 | Hermatic Door
|  | 1 | 2 |  |  | 2
C-123 | Aluminium False Ceiling
|  | 1 | 73092 |  |  | 73092
|  |  |  | Total Qty |  | 73092 | Sft
C-124 | UPVC Bumper Rail | 1 | 11302 |  |  | 11302
|  |  |  | Total Qty |  | 11302 | Rft
C-125 | Pvc Paneling
|  | 1 | 2500 |  |  | 2500 | Sft
C-126 | ACP
|  | 1 | 940 |  |  | 940 | Sft
C-127 | Color Crete
|  | 1 | 64003 |  |  | 64003 | Sft
C-128 | Nano Quartz
|  | 1 | 2500 |  |  | 2500 | Sft
C-129 | G.I Flashing Type -1 | 1 | 1000 |  |  | 1000 | Rft
C-130 | G.I Flashing Type -2 | 1 | 1000 |  |  | 1000 | Rft
C-131 | G.I Flashing Type -3 | 1 | 1000 |  |  | 1000 | Rft
C-132 | G.I Flashing Type -4 | 1 | 1000 |  |  | 1000 | Rft
C-133 | Sealent-1 | 1 | 4000 |  |  | 4000 | Rft
C-134 | Sealent-2
|  | 1 | 1000 |  |  | 1000 | Rft
C-135 | SBR Chemical
|  | 1 | 103797 |  |  | 103797 | Sft
C-136 | External Signage and Internal Signage
|  | 1 | 1 |  |  | 1 | Job
C-137 | Wall Graphics
|  | 1 | 750 |  |  | 750 | Sft
C-138 | S.S Edge Protection
|  | 1 | 500 |  |  | 500 | Rft
C-139 | Sika Seal
|  | 1 | 67537 |  |  | 67537 | Sft