Site Description: Waterkloof House Building, encompassing UNHCR Regional Bureau

# General Site Description

The UNHCR Regional Bureau Pretoria is situated in the Waterkloof House in Pretoria at the following coordinates.:

| Waterkloof House | 25.7539100° S | 28.2104200°E |
| --- | --- | --- |

Figure 1: Site location

The Waterkloof House building is a double storey structure plus basement and is occupied by UNHCR Regional Bureau and the Multi Country Office. The facility is located in Pretoria East, and the building appears to be in good and well-maintained condition. The roof structure is cliplock and in good condition.

The building supports approximately 165 UNHCR staff and consists only of offices and associated office infrastructure such as underground parking, toilets, safe, kitchens, cafeteria, toilets, meeting rooms.

|  | Figure 2: aerial view of Waterkloof House with panel overlay The rooftop of the Waterkloof House is suitable for PV panels, pending a structural assessment. Please refer to Annex B II. Technical Specifications for Waterkloof House for more info. |
| --- | --- |

# Waterkloof House Electrical Infrastructure

The main DB board is situated in the underground basement. The Main DB board does not have space to connect the proposed PV/Battery system and will require some bus bar changes in order to incorporate the injection points for the PV and Battery system.

There is a room 10 meters from the DB that is suitable to house the battery system

| Dedicated Transformer on site at Waterkloof House building. | Main Distribution Board |
| --- | --- |

# Existing infrastructure

The Waterkloof House building is connected to the national electrical grid, by 3ph - 800 A. In addition, due to extensive rotational load shedding, the office depends on the 500 kVA diesel generator to supply backup power. The generator system belongs to the landlord, and the fuel is paid for by UNHCR. The generator currently supplies between 10 -20% of the load requirements.

Table 1. Details of the diesel generator

|  | Gen 1 Perkins |
| --- | --- |
| Rated power | 500 kVA |
| Installed |  |
| Use | 2323 hours |
| Located | Outside Basement Entrance |

*The UNHCR generator maintenance is running every 400 hours for oil and filter change, 800 hours for air cleaner along with monthly inspection and on faults.

Figure 3: UNHCR generator changeover located outside the Waterkloof House building.

The diesel tank is filled by hand using 20 litre containers.

Figure 4: 500 kVA Perkins Diesel Engine

Figure 5: Floor Plan

# Information on existing supply contract

The UNHCR generator is serviced by a maintenance company each 400 working hours and on a monthly basis and/or on faults and damage. It is also monitored on a daily basis by UNHCR technical staff.

The facility is billed by Tshwane Municipality and the Tshwane Small Scale Embedded Generation regulations apply.

# Climate

Pretoria: The average temperature in Pretoria ranges from 2 – 35 degrees Celsius with rain and heavy thunderstorms during the summer season.

# Energy Load

Annual Electrical energy demand is 456 250 kWh, with more electricity consumed in the winter months, indicating heating load.

# Additional information

There is currently a 30 kVA UPS system installed that supplies power to a small, dedicated circuit during load shedding times. The system is old and needs replacing.