## 0-CoverPage
UNHCR Standard Commissioning Protocol
The commissioning protocol represents the minimum standards of commissioning and commissioning documentation and is required for the technical completion and handover of the PPS.
Cover Page
The Cover Page includes the project name and project reference, along with the commissioning date, any potential supplementary commissioning, and the approval of the commissioning.
Project Name
Ref. No.
Site Name
Frame agreement holder name
Local partner
Commissioning implemented by (name)
Date of commissioning
Commissioning protocol successfully completed (yes/no)
If no see: Snag List
Supplementary commissioning necessary (yes/no)
Supplementary Commissioning implemented by (name)
Date of supplementary commissioning
Supplementary Commissioning Protocol successfully completed (yes/no)
Commissioning / Supplementary commissioning approved by (name)
List of Content | List of Content
1 | Instructions
2 | List of participants
3 | BOQ (deliverables quoted vs. as built)
4 | Technical compliance (deliverables quoted vs. as built)
5 | System layout and technical documentation
6 | Visual Inspection
7 | Torque Inspection
8 | Electrical Tests
9 | Operational Tests
10 | Settings
11 | Training
12 | Snag List

## 1-Instructions
UNHCR Standard Commissioning Protocol
Instructions
In the following a brief introduction in the UNHCR Standard Commissioning Protocol is provided.
This UNHCR Standard Commissioning Protocol serves for the technical acceptance of the PPS delivered by the Contractor (Frame Agreement Holder).
This Protocol does not preclude any commissioning protocols as required by local regulations.
This Protocol is an internal UNHCR procedure for quality control and documentation purposes.
In addition to the Protocol, a complete documentation in both hardcopy and softcopy is required, including photo documentation.
The Contractor will provide the necessary measurement instruments for conducting the UNHCR Standard Commissioning Protocol. The Protocol will be executed and documented by the Contractor. UNHCR will appoint a representative to oversee the execution of the Protocol.
Elements, steps, etc., found to be unsatisfactory, need to be recorded in the Snag List. If there are points marked as unsatisfactory, a Supplementary Commissioning must be carried out. During this process, the functionality will be recorded and the Snag List will be reviewed.
Commissioning is approved with signature of the UNHCR representative at the cover sheet.

## 2-Participants
UNHCR Standard Commissioning Protocol
List of participants
The list of participants at commissioning has to be filled. In case there is open issues at the initial commissioning a supplementary commissioning will be necessary. The additional participant list needs to be filled.
Commissioning
Ref. | First name | Last name | Title | Organization / Company | Responsibility at commissioning
1
2
3
4
5
6
7
8
9
10
Supplementary commissioning (if applicable)
Ref. | Prename | Last name | Title | Organization / Company | Responsibility at commissioning
1
2
3
4
5
6
7
8
9
10

## 3-BOQ
UNHCR Standard Commissioning Protocol
BOQ (deliverables quoted vs. as built)
Note: Total as-built capacity must be validated against declared capacity.
[Type and Name of Office]
Item | Description | Unit | Specified Capacity | Proposed Capacity | As-built Capacity
Core items (ex work prices)
1 | Hybrid inverter incl cabling and protections | [kW]
2 | Charge regulators (MPPT) and protections - DC coupling Grid-tie string Inverter (MPPT) and protections - AC coupling | [kW]
3 | PV modules | [kWp]
4 | Lithium Iron Phosphate Batteries incl cabling and protections | [kWh]
5 | Battery Management System | Unit
6 | Monitoring and Metering System | Unit
7 | Solar panel cleaning kit & tool kit | Unit
TOTAL
Optional and variable items
Item | Description | Unit | Specified Capacity | Proposed Capacity | As-built Capacity
Mounting structure
8 | Static considerations of the mounting structure and base | Unit
9 | Roof mounting structure | [kWp]
Powerhouse
10 | Container | Unit
Cabling
11 | AC cable: 0-10m | m
12 | AC cable: 11-30m | m
13 | AC cable: 31-60m | m
14 | AC cable: >60m | m
15 | DC cable: 0-10m | m
16 | DC cable: 11-30m | m
17 | DC cable: 31-60m | m
18 | DC cable: >60m | m
Spare & Miscellaneous items (add any additional items by typing in the blue rows below)
19 | 5% spare solar PV modules | kWp
20 | 5% spare PV connectors | Unit
21 | 5% spare AC cable: 0-10m | m
22 | 5% spare AC cable: 11-30m | m
23 | 5% spare AC cable: 31-60m | m
24 | 5% spare AC cable: >60m | m
25 | 5% spare DC cable: 0-10m | m
26 | 5% spare DC cable: 11-30m | m
27 | 5% spare DC cable: 31-60m | m
28 | 5% spare DC cable: >60m | m
29 | Retrofitting of roofs if required
30 | Upgrades electrical distribution boards, connection points, change over switch, resp. electrical installation if required
31 | Additional item

## 4-TechCompliance
UNHCR Standard Commissioning Protocol
Technical compliance (deliverables quoted vs. as built)
Note: This document serves as a record of the primary components comprising the system. It is essential to include the technical specifications of the equipment. Furthermore, please ensure that a separate list of serial numbers for power components (inverters, battery modules, PV modules) is attached.
System as built
Component | Brand | Type | Quantity | Specification (nominal capacity/size, list of parts/sensors) | List of serial numbers attached (yes/no) | Comment

## 5-LayoutDocs
UNHCR Standard Commissioning Protocol
System layout and technical documentation
In this section, all necessary documents are listed and reviewed. The documents in "System layout" must correspond to the actual construction execution, as-built. The documents in 4.2 Technical Documentation will be checked for completeness.
System layout
Ref. | Item | Indication if NOT applicable (n.a.) | Name of original document | Control document number (assigned by UNHCR) | As built schematics submitted (yes/no) | As built schematics approved (yes/no) | Corrective measure (if applicable) | Comment
1 | Layout |  |  | [PPS-Country-OfficeType-Name-001]
2 | Layout mounting structure |  |  | [PPS-Country-OfficeType-Name-002]
3 | Powerhouse detailed drawing |  |  | [PPS-Country-OfficeType-Name-003]
4.1 | SLD: PV DC cables & protection |  |  | [PPS-Country-OfficeType-Name-004]
4.2 | SLD: Battery DC Cables & protection |  |  | [PPS-Country-OfficeType-Name-005]
4.4 | SLD: AC connection (PV, Batter, Genset, Grid, Switchboard, Main Distribution Board) |  |  | [PPS-Country-OfficeType-Name-006]
4.5 | Grounding and Lighting Protection |  |  | [PPS-Country-OfficeType-Name-007]
Technical documentation
Ref. | Item | Indication if NOT applicable (n.a.) | Name of original document | Control document number (assigned by UNHCR) | Checks reminder | Compliant (yes/no) | Corrective measure (if applicable) | Comment
5.1 | List of serial numbers - Inverters |  |  | [PPS-Country-OfficeType-Name-008]
5.2 | List of serial numbers - PV modules |  |  | [PPS-Country-OfficeType-Name-009]
5.3 | List of serial numbers - Battery modules |  |  | [PPS-Country-OfficeType-Name-010]
5.4 | List of serial numbers - Weather station |  |  | [PPS-Country-OfficeType-Name-011]
5.5 | List of serial numbers - Air conditioning |  |  | [PPS-Country-OfficeType-Name-012]
6.1 | Technical sheet - Inverters |  |  | [PPS-Country-OfficeType-Name-013]
6.2 | Technical sheet - PV modules |  |  | [PPS-Country-OfficeType-Name-014]
6.3 | Technical sheet - Battery modules |  |  | [PPS-Country-OfficeType-Name-015]
6.4 | Technical sheet - Weather station |  |  | [PPS-Country-OfficeType-Name-016]
6.5 | Technical sheet - Air conditioning |  |  | [PPS-Country-OfficeType-Name-017]
7.1 | Manufacturers operational, maintenance & trouble shooting manual - Inverters |  |  | [PPS-Country-OfficeType-Name-018]
7.2 | Manufacturers operational, maintenance & trouble shooting manual - PV modules |  |  | [PPS-Country-OfficeType-Name-019]
7.3 | Manufacturers operational, maintenance & trouble shooting manual - Batter modules |  |  | [PPS-Country-OfficeType-Name-020]
7.4 | Manufacturers operational, maintenance & trouble shooting manual - Weather station |  |  | [PPS-Country-OfficeType-Name-021]
7.5 | Manufacturers operational, maintenance & trouble shooting manual - Air conditioning |  |  | [PPS-Country-OfficeType-Name-022]
8.1 | Warranty document - Inverter |  |  | [PPS-Country-OfficeType-Name-023] | Stated serial number must be controlled on site
8.2 | Warranty document - PV modules |  |  | [PPS-Country-OfficeType-Name-024] | Stated serial number must be controlled on site
8.3 | Warranty document - Battery modules |  |  | [PPS-Country-OfficeType-Name-025] | Stated serial number must be controlled on site
8.4 | Warranty document - Weather station |  |  | [PPS-Country-OfficeType-Name-026] | Stated serial number must be controlled on site
8.5 | Warranty document - Air conditioning |  |  | [PPS-Country-OfficeType-Name-027] | Stated serial number must be controlled on site
8.6 | Warranty document - System level |  |  | [PPS-Country-OfficeType-Name-028] | Stated serial number must be controlled on site
9.1 | Quality Assurance Manual |  |  | [PPS-Country-OfficeType-Name-029] | Labeling in the manual must be controlled with labeling on site
9.2 | Safety Manual |  |  | [PPS-Country-OfficeType-Name-030] | Labeling in the manual must be controlled with labeling on site
9.3 | Operations Manual |  |  | [PPS-Country-OfficeType-Name-031] | Labeling in the manual must be controlled with labeling on site
9.4 | Training Manual |  |  | [PPS-Country-OfficeType-Name-032] | Labeling in the manual must be controlled with labeling on site
9.5 | After Sales Service Specifications including preventing and corrective maintenance, tasks, responsible people, list of materials and tools required |  |  | [PPS-Country-OfficeType-Name-033] | Labeling in the manual must be controlled with labeling on site
[PPS-Country-OfficeType-Name-034]

## 6-Visual
UNHCR Standard Commissioning Protocol
Visual Inspection
In this section, essential elements of the visual inspection are listed. All steps must be conducted and recorded.
System components as built
Component | Specification | Indication if NOT applicable (n/a) | Inspection passed (yes/no) | Corrective measure (if applicable) | Comment
PV Modules | No major shading on PV modules
PV Modules | All modules aligned correctly (alignment, horizontal, vertical, level, etc.)
PV Modules | No visual defects on modules (scratches, cracks, corrosion, hot spots, moisture behind glass, breaks on the backside, delamination, etc.)
PV Modules | Junction box on backside properly sealed, no hot spot
PV Modules | PV module attachments to the structure are tight and the modules are fully seated
PV DC Cabling | The output from the solar PV module connections have the correct polarity
PV DC Cabling | Proper connectors on array wiring extensions
PV DC Cabling | Cable size according to standard defined for the site (compare Technical Compliance)
PV DC Cabling | Cabling properly insulated
PV DC Cabling | Cable routing is properly conducted (protection from UV, conduits used where required, no cable hanging around freely)
PV DC Cabling | Conduits are covered and holes sealed
PV String combiner | The electrical continuity and polarity checked for all strings
PV String combiner | A string combiner box with protections installed
PV String combiner | The Surge Protection Device in the String Combiner Box has not been "arrested" (i.e. the check window is in green color and NOT red)
PV String combiner | The Surge Protection Device has a conductive path to ground
PV String combiner | All main elements are clearly identified and labeled
PV System Mounting | Mounting system has been installed according to the drawings provided by the manufacturer and layout approved
PV System Mounting | The structure is well anchored to the roof and there are no loose parts
PV System Mounting | Mounting structure electrically grounded
PV System Mounting | Roof sealing secured (no broken tiles, sealing used for screws, etc.)
Hybrid / PV / Battery Inverter | No physical damage (visual inspection of the batteries to check for defects, cracks, leaks, the integrity of the enclosure, and support structure)
Hybrid / PV / Battery Inverter | All electronic components are securely installed in the designated technical room/space
Hybrid / PV / Battery Inverter | The inverter has been installed according to the manufacturer's manual
Hybrid / PV / Battery Inverter | A grounding cable is connected between the equipment housing/frame and the grounding/earthing bus
Hybrid / PV / Battery Inverter | All cables are connected tightly and using correct terminations (cables shoes, lugs,…) of appropriate size
Hybrid / PV / Battery Inverter | The solar PV array is connected to the PV-Input of the inverter with the correct polarity
Hybrid / PV / Battery Inverter | The grid connection from the Main Distribution Board is connected to the AC breaker labeled "Grid" on the inverter
Hybrid / PV / Battery Inverter | The genset connection from the Main Distribution Board is connected to the AC breaker labeled "Genset" on the inverter
Hybrid / PV / Battery Inverter | All inverters are clearly identified and labeled
PV AC cable | Visual inspection (insulation, routing)
PV communication cables | Visual inspection (insulation, routing)
Battery communication cables | Visual inspection (insulation, routing)
Battery | No physical damage (check for any signs of wearing or damage like Cracks, damaged terminals, inflated signs, sulfide flakes at terminals, or any physical damage)
Battery | Check battery racks/Cabinet assembled and installed as per manufacturer’s instruction and drawings
Battery | Check battery is installed in accordance with the manufacturer's instructions with sufficient clearance and accessibility for maintenance
Battery | Surge protection in place and all main elements of the protective devices are clearly identified and labeled
Battery | Earthing in place
Battery | Check battery cells are identified and tagged correctly
Battery | Check battery data against data sheet/project specification
Battery | Check all the nuts and links are fitted, tightened, torqued greased, and covered with terminal covers
Battery | Check caps for transportation have been removed
Battery | Check cell interconnections against drawings
Battery | Check terminal protection covers are installed
Battery | Check cable size and connections and polarity checked
Battery | Check the material for battery rack materials as per the approved drawing and has corrosion-proof coating (factory test certificate)
Battery | Verify all the battery racks are grounded
Battery | Check the protective terminal covers are installed after terminating the battery cables and secured
Battery | Verify the accessibility of all battery cells for routine maintenance
Battery | All battery components are clearly identified and labeled
Air conditioning | No physical damage
Air conditioning | Air filters in place
Air conditioning | All main elements are clearly identified and labeled
Fire detection and suppression system | No physical damage
Fire detection and suppression system | All main elements are clearly identified and labeled
Emergency switch | Emergency switch directly accessible and is clearly marked and labelled
Electrical Cabinets | There is no visible damage in any of the breakers, like burning, corrosion.
Electrical Cabinets | Safe installation (finger safety, closure, etc.)
Electrical Cabinets | Terminals fixed properly, no hot spots
Electrical Cabinets | The existing distribution system is connected to the output circuit breaker of the AC distribution box and labeled as "load"
Electrical Cabinets | The AC output of the inverter is connected to the existing electric distribution system by a circuit breaker
Electrical Cabinets | There is an AC contactor ("relay") installed at the output of the inverters that closes the circuit only when the Grid is ON
Electrical Cabinets | The Surge Protection Device in the AC Distribution board has not been "arrested" (i.e. the check window is in green color and NOT red)
Electrical Cabinets | The AC Distribution board(s) are grounded
Electrical Cabinets | All the electric boxes, with its breakers, switches, fuses, surge protection devices and all the electric distribution boards (AC and DC), and all the system components are clearly identified and labeled.
Container | No physical damage
Container | Proper installation surface (secure against water, or flooding, accessibility, etc.)
Container | Container lockable
Container | All the electric boxes, with its breakers, switches, fuses and all the electric distribution boards (AC and DC), and all the system components are clearly identified and labeled.
Weather station | No physical damage
Weather station | Weather sensors mounted properly (tight installation, no obstacles in the vicinity)
Weather station | Earthing in place
Weather station | All main elements are clearly identified and labeled
Monitoring System | The screen and the LED lights of the inverter show normal operation mode and there is no alarm
Monitoring System | The LED lights of the datalogger device indicate normal operation mode and there are no alarms
Monitoring System | After its registration, the PV system with its parameters is present in the online monitoring system

## 7-Torque
UNHCR Standard Commissioning Protocol
Torque Inspection
This section describes the fastening tests to be conducted. For this purpose, the technically correct attachment of mechanical elements must be checked using appropriate tools such as a wrench, allen key, torque wrench, etc.
System components as built
Component | Specification | Indication if NOT applicable (n/a) | Number of samples tested | Inspection passed (yes/no) | Comment
PV Modules | Testing the fastening of the module clamp and the attachment of PV modules to the mounting system. For this purpose, 10% of the modules must be tested for secure installation using an appropriate tool.
PV Module Mounting | Testing the fastening of the mounting system. The technical execution of the mounting system must be examined. For this purpose, screw fastenings will be inspected at regular distance intervals (every 5 m, horizontally).
Hybrid / PV / Battery Inverter | The technically correct attachment is checked. Where possible, the screw fastening is checked.
Battery Modules | The technically correct attachment is checked. Where possible, the screw fastening is checked.
Weather sensors (station) | The technically correct attachment is checked.
Electric cabinet | The technically correct attachment is checked. Where possible, the screw fastening is checked.

## 8-Measurements
UNHCR Standard Commissioning Protocol
Electrical Tests
During commissioning, electrical measurements must be conducted and documented. Below is a list of the measurements to be performed.
Earthing test
Indication if NOT applicable (n.a.) | Please add a brief description of the measurement.
Equipment Ref. | Brand of measurement equipment |  | Type of Measurement equipment |  | Certification (if applicable) | Date of certification (if applicable)
E-E1
E-E2
Measurement Ref. | Indication if NOT applicable (n.a.) | Name of System | Measured value of earth resistance | Earth resistance < 10 Ohm (yes/no) | Inspection passed (yes/no) | Comment
M-E1
M-E2
M-E3
M-E4
Insulation test
Indication if NOT applicable (n.a.) | Please add a brief description of the measurement.
Equipment Ref. | Brand of measurement equipment |  | Type of Measurement equipment |  | Certification (if applicable) | Date of certification (if applicable)
E-I1
E-I2
Measurement Ref. | Name of System | Measured insulation resistance |  |  | Inspection passed (yes/no) | Comment
M-I1
M-I2
M-I3
M-I4
M-I5
RCD test
Indication if NOT applicable (n.a.) | Please add a brief description of the measurement.
Equipment Ref. | Brand of measurement equipment |  | Type of Measurement equipment |  | Certification (if applicable) | Date of certification (if applicable)
E-RCD1
E-RCD2
Measurement Ref. | Name of System | Trip time RCD (if applicable) |  |  | Inspection passed (yes/no) | Comment
M-RCD1
M-RCD2
M-RCD3
M-RCD4
Battery (full cycle test)
Indication if NOT applicable (n.a.) | Please add a brief description of the measurement.
Equipment Ref. | Brand of measurement equipment |  | Type of Measurement equipment |  | Certification (if applicable) | Date of certification (if applicable)
E-BC1
E-BC2
Measurement Ref. | Name of System | Full Cycle Test (Capacity in kWh) | Charge current in A @ Temperature in C° | Disharge current in A @ Temperature in C° | Inspection passed (yes/no) | Comment
M-BC1
M-BC2
M-BC3
M-BC4
Battery (total values)
Indication if NOT applicable (n.a.) | Please add a brief description of the measurement.
Equipment Ref. | Brand of measurement equipment |  | Type of Measurement equipment |  | Certification (if applicable) | Date of certification (if applicable)
E-BSOH1
E-BSOH2
Measurement Ref. | Name of System | Total cylces recorded | State of Health |  | Inspection passed (yes/no) | Comment
M-BSOH1
M-BSOH2
M-BSOH3
M-BSOH4
Battery module tests
Indication if NOT applicable (n.a.) | Please add a brief description of the measurement.
Equipment Ref. | Brand of measurement equipment |  | Type of Measurement equipment |  | Certification (if applicable) | Date of certification (if applicable)
E-BM1
E-BM2
Measurement Ref. | Name of System | Resistance measured (in Ohm) | Thermographic measurement (in C°) | Communication to BMS confirmed (yes/no) | Inspection passed (yes/no) | Comment
M-BM1
M-BM2
M-BM3
M-BM4
M-BM5
M-BM6
M-BM7
M-BM8
M-BM9
M-BM10
M-BM11
M-BM12
M-BM13
M-BM14
M-BM15
M-BM16
M-BM17
M-BM18
M-BM19
M-BM20
M-BM21
M-BM22
M-BM23
M-BM24
M-BM25
PV (OS, SC)
Indication if NOT applicable (n.a.) | Please add a brief description of the measurement.
Equipment Ref. | Brand of measurement equipment |  | Type of Measurement equipment |  | Certification (if applicable) | Date of certification (if applicable)
E-PV1
E-PV2
Measurement Ref. | Name of System and String | Open Circuit Voltage (V) | Short Circuit Current (A) | Insulation Resistance (Ohm) | Inspection passed (yes/no) | Comment
M-PV1
M-PV2
M-PV3
M-PV4
M-PV5
M-PV6
M-PV7
M-PV8
M-PV9
M-PV10
M-PV11
M-PV12
M-PV13
M-PV14
M-PV15
M-PV16
M-PV17
M-PV18
M-PV19
M-PV20
M-PV21
M-PV22
M-PV23
M-PV24
M-PV25
PV (MPP)
Indication if NOT applicable (n.a.) | Please add a brief description of the measurement.
Equipment Ref. | Brand of measurement equipment |  | Type of Measurement equipment |  | Certification (if applicable) | Date of certification (if applicable)
E-PVMPP1
E-PVMPP2
Measurement Ref. | Name of System and String | Voltage at maximum power point (V) | Current at maximum power point (I) | Temperature at measured maximum power point (C°) | Inspection passed (yes/no) | Comment
M-PVMPP1
M-PVMPP2
M-PVMPP3
M-PVMPP4
M-PVMPP5
M-PVMPP6
M-PVMPP7
M-PVMPP8
M-PVMPP9
M-PVMPP10
M-PVMPP11
M-PVMPP12
M-PVMPP13
M-PVMPP14
M-PVMPP15
M-PVMPP16
M-PVMPP17
M-PVMPP18
M-PVMPP19
M-PVMPP20
M-PVMPP21
M-PVMPP22
M-PVMPP23
M-PVMPP24
M-PVMPP25

## 9-Operation
UNHCR Standard Commissioning Protocol
Operational Tests
Safety functions and operating modes need to be tested. The execution and documentation of these tests are essential.
Safety tests
Event | Indication if NOT applicable (n.a.) | Descripton of system reaction |  |  | Compliant (yes/no) | Comment
Activate emergency button
Trip AC surge
Disconnect system remotly
Test grid blackout
Test genset blackout
Test battery stop and extinguishing mechanism
Normal operation procedures
Procedure | Indication if NOT applicable (n.a.) | Description of event |  |  | Compliant (yes/no) | Comment
Full system startup
PV power is injected into the AC bus to lower consumption from the grid
PV power is not available (simulating by turning off inverter breakers), but grid power is available, the grid is used to power the loads
PV power returns (turning on inverter breakers), solar inverters start to inject energy into the AC bus again
No solar power available (simulated by the PV breaker off) and the grid fails (simulated by turning off the "grid" breaker), the loads are powered by the genset
Loads are powered by the genset, the inverters work with the genset
Battery discharge without PV
Battery charge by grid (without PV)
Battery charge by genset (without PV)
System blackstart at grid blackout (if applicable)
System blackstart at genset blackout (if applicable)
The presented values (voltage, current, etc.) match with measurements and the actual operation mode.
Manual Change Over switch
Normal operation observations
Component | Indication if NOT applicable (n.a.) |  |  |  | Compliant (yes/no) | Comment
Air conditioning effectively operational
Air ventilation at inverter effectively operational
Air ventilation at container effectively operational
Operation of weather station
Procedure | Indication if NOT applicable (n.a.) |  |  |  | Compliant (yes/no) | Comment
Sensors calibrated
Sensor data online / available
Monitoring System
Category | Indication if NOT applicable (n.a.) | Descripton of Parameter | Availability of historical data | Sampling rate | Inspection passed (yes/no) | Comment
Status monitoring of all active system components
Technical monitoring system
Managerial monitoring system
Metering for charging purposes
System event logs
Alarming

## 10-Settings
UNHCR Standard Commissioning Protocol
Settings
Parameters and settings of the component and system level, the hardware and the software of the PPS are documented in this section.
Inverter settings
The Grid Code parameters must be listed. Additionally, parameterization codes, and communications settings including parameterization access (admin, installer, standard user, guest account) details need to included.
Parameter | Parameter description | Value
System level & controller settings
System paramters (example min state of charge) needs to be listed. Additionally, parameterization codes, and communications settings including parameterization access (admin, installer, standard user, guest account) details need to included.
Parameter | Parameter description | Value
Monitoring settings
Monitoring settings needs to be listed. Additionally, parameterization codes, and communications settings including parameterization access (admin, installer, standard user, guest account) details need to included.
Parameter | Parameter description | Value

## 11-Training
UNHCR Standard Commissioning Protocol
Training
In this section, the execution of training will be documented.
Training content
Ref. | Training content | Specification |  | Training element covered (yes/no) | Comment
T11 | Safety and Introduction to the system | Basic safety rules
T12 |  | Basics in solar energy off-grid systems and PPS
T13 |  | Identifying components (on site & schematics)
T14 |  | Component functionalities
T15 |  | System functionalities
T16 |  | Danger in misusing components / system
T21 | Operating the system | Operation of the system with hardware tests on site
T22 |  | Reading and understanding manual and schematics
T23 |  | Display, Signals & buttons
T24 |  | Practical exercises by individual participants
T31 | Preventive actions | Tasks to prevent system from malfunctioning (overload, connecting faulty equipment, power cords, etc.)
T32 |  | Effects of misusing system components
T33 |  | System performance and optimization
T34 |  | Trouble shooting and problem solving
T35 |  | Identification of alarms
T36 |  | Restart of system
T37 |  | Recording trouble shooting
T41 | Remote control and monitoring | Monitoring principle
T42 |  | Monitoring functionalities
T43 |  | Remote control functionalities
T51 | After sales service steps | Fault types
T52 |  | Frequency of maintenance
T53 |  | Description of maintenance tasks
T61 | Exercise in site & best practices | Operational steps performed by individuals
T62 |  | Trouble shooting performed by individuals
T63 |  | Maintenance performed by individuals
T71 | Manuals (Operations, After Sales, Training) | Basics and usability
1. List of Participants - Training
Ref. | First name | Last name | Title | Organization / Company | Responsibility during system operation and maintenance
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20

## 12-SnagList
UNHCR Standard Commissioning Protocol
Snag List
Elements requiring rework and correction will be listed in the Snag List. During Supplementary Commissioning, the Snag List will be explicitly reviewed.
Ref. | Topic | Specification | Measurement value | Corrected on (date) | Corrected by (name)
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20