Borehole Drilling and Test Pumping Specifications

CONTRACT #___________________

DATE             ___________________

This document is a technical specification that should accompany a standard UNHCR Contract.  It required review and modification to fit the exact works required.  All those areas with red text need to be adjusted. This paragraph should be removed from the final document.

TECHNICAL SPECIFICATIONS

1.	SCOPE OF WORK	3

2.	GENERAL REQUIREMENTS	3

2.1	GENERAL	3

2.2	SITING OF BOREHOLES	4

2.3	BOREHOLE IDENTIFICATION	4

2.4	GEOLOGICAL AND HYDROGEOLOGICAL CONDITIONS	4

2.5	BOREHOLE DESIGN	4

2.6	CONSTRUCTION PROGRAM	5

3.	MATERIAL REQUIREMENTS	5

3.1	FIELD EQUIPMENT	5

3.2	STORAGE OF MATERIALS	5

3.3	TOXIC MATERIALS	5

4.	BOREHOLE CONSTRUCTION REQUIREMENTS	5

4.1	ERECTION OF DRILLING RIG	5

4.2	BOREHOLE DEPTH AND BOREHOLE DESIGN	5

4.3	DRILLING SEQUENCES	6

4.4	REAMING OF BOREHOLES* (* if applicable)	6

4.5	ASSEMBLING OF CASING	6

4.6	CENTRALISERS	6

4.7	FAILURE OF CASING STRING INSTALLATION	6

4.8	VERTICALITY AND ALIGNMENT OF BOREHOLES	7

4.9	FAILURE OF CASING STRING INSTALLATION	7

4.10	CHARACTERISTICS OF THE BOREHOLE CONSTRUCTION MATERIALS	7

4.10.1	DRILLING FLUID AND ADDITIVES* (*if applicable, i.e. if drilling with fluids)	7

4.10.2	CHARACTERISTICS OF THE CASING AND SCREENS	8

4.10.3	CHARACTERISTICS OF CEMENT AND CONCRETE (*if applicable)	8

4.10.4	GRAVEL PACKING, BENTONITE AND PARTIAL BACKFILLING OF BOREHOLES	8

5.	BOREHOLE COMPLETION REQUIREMENTS	9

5.1	BOREHOLE DEVELOPMENT	9

5.2	PUMP TESTING REQUIREMENTS	9

5.2.1	CALIBRATION TEST AND TEST DISCHARGE RATE DESIGN	10

5.2.2	STEP DRAW-DOWN TEST	11

5.2.3	CONSTANT RATE PUMPING TEST	11

5.3	SANITARY SEAL	12

5.4	HEAD AND CAPPING	12

5.5	CLEAN-UP AND CONTAMINATION PREVENTION	12

6.	MONITORING, SAMPLING AND LOGGING REQUIREMENTS	13

6.1	DRILLING FLUID MONITORING	13

6.2	BOREHOLE LOGGING	13

6.3	FORMATION SAMPLING	13

6.4	PUMP TEST MONITORING	13

6.4.1	WATER LEVEL MONITORING	14

6.4.2	FLOW RATE MONITORING	14

6.4.3	WATER QUALITY MONITORING AND WATER SAMPLING	14

7.	REPORTING REQUIREMENTS	14

APPENDIX 1: TECHNICAL DRAWINGS: BOREHOLE DESIGN,  WELLHEAD AND CAPPING	16

APPENDIX 2: STANDARD PUMP TEST FORMS	19

APPENDIX 3: STANDARD BOREHOLE LOG AND QUALITY CONTROL CHECK LIST	20

## SCOPE OF WORK

The work required by this contract includes the construction of [ENTER NUMBER OF BOREHOLES] production borehole(s), and or [ENTER NUMBER OF MONITORING BORES] monitoring boreholes according to the borehole design provided by the EMPLOYER and amended to this contract (Appendix 1).

[Exact description of the drilling works to be carried out, according to the borehole design (Appendix 1)]

The construction work comprises the following tasks [DESCRIPTION OF THE MAIN ACTIVITIES OF THEW WORKS]:

- Drill a hole of [XX inch] diameter to the depth of [XX meters] and install and cement [XX meters] of [XX inch] surface casing

- Drill a borehole to [X meters] of [XX inch] diameters and install [XX-inch diameter and type] of casing

During drilling, water strikes and estimated yields (dependent on method of drilling adopted), electroconductivity (EC) and pH of the drilling-returned water will be measured at regular intervals, drilling penetration rates will be recorded and lithological samples will be bagged and described, according to section 6.3.

The Test Pumping Operations will comprise a calibration test, a step-test, a constant rate test and a recovery period, to be carried out according to section 5.2.

## GENERAL REQUIREMENTS

### GENERAL

Any Works whether shown on the Drawings and/or described in the Specifications but which can reasonably be inferred as necessary for the completion and proper operation of the works will also form part of the extent of the Contract.

Materials and works not covered by these specifications will be specified either in the conditions, Drawings or in the Bill of Quantities (BoQ) (Appendix 1).

The General and Special Specifications shall be read together in conjunction with the Bills of Quantities, Drawings and other Tender Documents, which shall be considered as mutually explanatory.

Prior to the commencement of the work for all items, the CONTRACTOR shall submit a method statement to the EMPLOYER for approval. This shall include but is not limited to details of the arrangements and methods which the CONTRACTOR proposes to adopt for the execution of the works. No significant alteration to these arrangements and methods set forth in the Method Statement shall be made without this having previously been notified to and approved by the EMPLOYER in writing, which approval shall not be unreasonably denied.

### SITING OF BOREHOLES

The exact location of each borehole will be clearly marked in the field by the EMPLOYER in presence of the CONTRACTOR.  The CONTRACTOR is responsible for capturing the latitude and longitude using a GPS unit.

### BOREHOLE IDENTIFICATION

The borehole identification (ID) of each borehole has to be defined prior to drilling. The borehole identification stated on the drilling permit and/or a local borehole or Borehole ID must be clearly indicated on the borehole location in the field and systematically used in all documentation along with the GPS coordinates captured in Section 2.2.

### GEOLOGICAL AND HYDROGEOLOGICAL CONDITIONS

The geological units for Borehole XX that are expected to be encountered are [XX], at the [XX] depths and the static water level is expected to be at [XX] meters depths.

### BOREHOLE DESIGN

The complete borehole design is an integral part of the technical specification of this contract (Appendix 1). The EMPLOYER is responsible for the borehole design and for approval by the relevant authorities (i.e. drilling permit). The CONTRACTOR may, upon request by UNHCR, offer an alternative borehole design based on its experience of ground conditions within the target area and or hydrogeological/geophysical surveys conducted by the Contractor or a third party independent expert.  This alternative can only be implemented if approved in writing by the EMPLOYER and the relevant authorities.

### CONSTRUCTION PROGRAM

Within [XX] days of the order to commence the CONTRACTOR shall provide the EMPLOYER with:

- A scheme of the overall organization of the works and construction program, methods and material specifications; and

- A schedule of proposed dates, from shipment and site delivery of all items required for the temporary works and permanent works.

## MATERIAL REQUIREMENTS

### FIELD EQUIPMENT

The CONTRACTOR shall provide, deliver and maintain for use of the ENGINEER and for the duration of the works at an agreed location on the work site all the necessary equipment, apparatus, fittings, materials and supplies (e.g. sample bags, EC and pH meters, turbidity tube, dip meter, marsh funnel, water sample bottles, boxes for sampling, etc.) to carry out the required tests as described in section 6 and allow the ENGINEER to witness testing. All the equipment and tools shall be in good condition, calibrated and tested prior to onset of works.

### STORAGE OF MATERIALS

The CONTRACTOR shall store all materials shall be stored in a clean place, either in the open or under cover, especially any PVC material.

### TOXIC MATERIALS

The CONTRACTOR is prohibited to use any toxic or poisonous materials or sub-materials used in piping, its accessories, lining, coating, sealing etc., or in various kinds of concrete or in soil in any kind of usage.

## BOREHOLE CONSTRUCTION REQUIREMENTS

### ERECTION OF DRILLING RIG

The drilling machine must be erected at the borehole site in such a way that the hole will be drilled within 1 m of the clearly marked drilling position (2.2).

### BOREHOLE DEPTH AND BOREHOLE DESIGN

All technical details on drilling and casing diameters are given in the borehole design, APPENDIX A.

The boreholes to be drilled will be required to penetrate thickness less than XX meters of soil or poorly consolidated sediments. The surface casing shall be installed up to XX-meter-deep and not less than 5 meters deep. The drilling diameter for surface casing shall be at least XX-inch diameter and the surface casing should be at least XX-inch diameter.  The total depth of the borehole shall be XX meters.

### DRILLING SEQUENCES

The expected drilling sequence is [detailed description of drilling sequence, including all drilling diameters, the sequence of installation of casings etc]

### REAMING OF BOREHOLES* (* if applicable)

All reaming will be carried out with hole openers which are designed specifically for reaming or with bits which have been modified for reaming in a manner approved by the ENGINEER. Care will be taken to ensure that reaming work results in boreholes which are properly aligned and straight and concentric to the original borehole.

### ASSEMBLING OF CASING

The assembling methodology for casing will be submitted to and approved by the ENGINEER before operation. A particular attention will be paid to the external diameter of casing and its compatibility with cementing and gravel pack insertion. The casing shall be coupled to each other either with (i) welds or (ii) threaded connectors. If welding is done and in order to secure mechanical and corrosion resistances, the CONTRACTOR shall submit the certificates and qualifications of the welding operator to the ENGINEER and get his approval before starting operations. All welding electrodes must comply with the Standard Specifications standards. For threaded connections, the lubricating compound will not contain any heavy metal or hydrocarbons.

### CENTRALISERS

In order to achieve the required borehole linearity, all casing permanently installed in boreholes should be fitted with centralisers at 6-9 m intervals or as otherwise directed by the ENGINEER. The centralisers should be factory manufactured and shall not be installed within screened sections.

### FAILURE OF CASING STRING INSTALLATION

In the event that any string of casing will not enter the borehole, the casing will be removed, and the borehole will be reamed or re-drilled. If the string of casing still does not enter the borehole, the borehole will be declared lost by the CONTRACTOR.

### VERTICALITY AND ALIGNMENT OF BOREHOLES

The borehole(s) will be drilled and cased straight and vertical, and all casing will be set plumb and true to line. Upon completion of drilling or at any other time, the casing of the borehole shall be tested for verticality and straightness using a deviation-measuring device such as a dummy provided and operated by the CONTRACTOR.  Should the borehole vary from the vertical preventing the borehole shall be corrected by the CONTRACTOR at its own expense.

Should the CONTRACTOR fail to correct such faulty alignment or verticality, the borehole may be deemed lost if correct casing installation is not possible. The ENGINEER may waive the requirements of this paragraph for verticality if, in his judgment:

- The CONTRACTOR has exercised all possible care in constructing the borehole and the defect is due to circumstances beyond his control; or

- The usefulness of the completed borehole will not be materially affected.

In no event will the provisions of this paragraph with respect to alignment be waived.

### FAILURE OF CASING STRING INSTALLATION

In the event that any string of casing will not enter the borehole, the casing will be removed, and the borehole will be reamed or re-drilled. If the string of casing still does not enter the borehole, then the borehole is declared lost by the CONTRACTOR.

### CHARACTERISTICS OF THE BOREHOLE CONSTRUCTION MATERIALS

Any equipment or material introduced into the ground, whether on a temporary or permanent basis has to fulfil the below requirements.

#### DRILLING FLUID AND ADDITIVES* (*if applicable, i.e. if drilling with fluids)

The choice of drilling mud has to be in accordance with the legal regulations and may either be inorganic (bentonite) or of biodegradable type and non-toxic and amenable to degradation by an appropriate chemical agent and in accordance to the legal regulations The CONTRACTOR must ensure he has the necessary equipment including mud pumps, viscosity-measuring apparatus (e.g. marsh funnel), water tanks etc., to enable him to successfully complete the works. In case of use of drilling fluid, the mud pump should be able to ensure a 30 m/min ascending velocity of the fluid.

The CONTRACTOR shall specify the brand name and manufacturer of any mud or chemicals or additives proposed to be used and include technical specifications or any other relevant data.

- [Brand and type. Chemical composition if applicable];

#### CHARACTERISTICS OF THE CASING AND SCREENS

The XX-inch surface casing can be standard steel casing.

The XX-inch casing characteristics should be:

- [Brand and standard];

- the minimum collapse Strength will be [XX] bars; and

- connections are [type].

The technical specifications of all casings supplied by the CONTRACTOR which will be installed permanently in the boreholes must be new and must be provided and comply with international standards. The screen openings have to be appropriate (always smaller) than the grain size of the gravel pack (6.9.4).

#### CHARACTERISTICS OF CEMENT AND CONCRETE (*if applicable)

Cement: Any cement, which is used, must comply with ISO standards and must not be older than three months. Unless otherwise instructed by the ENGINEER, a hardening agent such as calcium chloride should not be used to accelerate the cement setting process.

Cement slurry: The cement used for cement slurry will be PORTLAND type. No less than 800 kg of cement will be used per cubic meter of water.

Cement mortar: The cement used for cement mortar will be PORTLAND type. No less than 50 kg of cement will be used for 100 l of water. A minimum of 600 kg of cement shall be used per cubic meter of sand.

Concrete: Concrete will be a mixture of Portland cement and aggregates (with only small amount of fine material) of not less than 250 kilograms per cubic metre of finished concrete. Aggregates used will be sound, durable and well graded in sizes ranging from sands to boulders of four centimetres. Concrete mixtures will contain no more than 30 litres of water per 50 kilograms of cement. Concrete will be measured by the cubic metre, and will be mixed in approved mixers or in mixing boxes and not directly on the ground.

Water for cement and concrete: The water used shall be potable water or be of a suitable quality to allow mixing of good quality cement and concrete, avoiding any introduction of substances with health hazard into the subsurface.

#### GRAVEL PACKING, BENTONITE AND PARTIAL BACKFILLING OF BOREHOLES

All gravel pack material should be made of well-rounded and well-sorted grains of inert material. The gravel needs to be clean and washed. It should be uniformly placed in the annular space between the screen and the borehole wall. The volume of introduced material has to be monitored and cross-validated with the calculated annular space.

For the gravel pack used in the screened sections, the gravel pack grain size and gradation are determined by the CONTRACTOR after analysis of the drill cuttings and the drillers log (formation stability, penetration rate, fluid loss and returns) and must be approved by the ENGINEER. The grain sizes have to be larger than the slots of the screened casing (6.9.2). In plain casing sections, gravel pack is used as formation stabiliser.

If a lower aquifer is targeted, then a bentonite seal (expanding granules, minimum length 2 meters) is introduced in the annular space just above screened sections to prevent mixing of groundwater of different aquifers.

Bentonite granules or cement are used to fill the annular space of the unsaturated zone, or at least the uppermost 5 meters until 1 meter below surface.

The CONTRACTOR shall, upon request,  backfill the existing borehole to a depth specified by the ENGINEER. The backfill material will consist of clean crushed or graded gravel. All such backfill material must be approved by the ENGINEER before being used in the borehole.

## BOREHOLE COMPLETION REQUIREMENTS

### BOREHOLE DEVELOPMENT

Borehole development will be conducted using a [airlift, or otherwise to be specified] system with an appropriate compressor. The borehole development method must be described in the work plan (section 2.6) and approved by the EMPLOYER.

Development shall continue until water is clean, but at least 6 hours. The development shall be monitored by measuring the discharge rate and the sand content at 15-30 minute intervals. Development shall not stop until the discharge water is clean and free of sand (i.e. less than 1 cm diameter with sand stain test in a 10 litre bucket, approximately 1ppm) and the discharge rate is stable for at least 2 hours or until the ENGINEER finds acceptable.

### PUMP TESTING REQUIREMENTS

The aquifer pumping test characterises the borehole performance and the water bearing formation in the vicinity of the borehole. The CONTRACTOR must correctly monitor test pumping operations to ensure that accurate data is obtained. For testing operations, the test pump will be installed in the pump housing defined in the borehole design (APPENDIX 1).

For the purpose of calibration and pump testing, the CONTRACTOR provides a range of pumps and valves to regulate the flow to produce [XX cubic meters per hour (m3/h)] against XX meters of pressure head. The CONTRACTOR provides all accessories required to install, operate and uninstall these pumping units, such as electric cable, electric panel control and exhaust pipes.

The pumped water during calibration and pumping tests must be disposed by means of discharge pipes toward a nearby natural drain over a distance where infiltration in to the aquifer during testing is negligible (minimum 50 meters and discharging downstream). No pools shall be allowed to form in the vicinity of the borehole to avoid re-infiltration.

During the tests, the CONTRACTOR shall measure and record water levels with the recommended frequency defined in the standard sheet ( APPENDIX 2) in the pumped borehole by means of an installed PVC-airline (dip tube) with a well-defined datum for measurement within an accuracy of +/- 1 cm and recorded.. For measurement of water levels, electric dip meters shall be used.

For discharge measurements, a flow meter shall be installed and calibrated/cross-validated with manual volumetric measurements and the measurements recorded with the recommended frequency defined in the standard sheet (APPENDIX 2). The discharge rate during the pumping shall be maintained within ten per cent (10%) of the design rates established with the calibration test (Section 5.2.1) and approved by the ENGINEER and the CONTRACTOR shall maintain uninterrupted pumping during the period of all tests.

Should the CONTRACTOR fail to provide accurate water level and flow measurements, then the ENGINEER may declare the test as interrupted and the CONTRACTOR has to repeat the test at their own expense. Unless otherwise directed by the Engineer, interrupted tests shall not be restarted until sufficient time has elapsed for at least ninety-five percent (95%) recovery of the water levels in the pump or observation borehole and shall not be considered to be a part of the pumping test for purposes of payment even though water level measurements shall be made during that period by the CONTRACTOR.

#### CALIBRATION TEST AND TEST DISCHARGE RATE DESIGN

Before beginning the pumping tests, a calibration test must be carried out to check that all equipment including the pump, generator, manometer, flow regulation valves and pipes are working satisfactorily. This test is also required to design the discharge rates for the step draw-down pumping test. The discharge pipeline shall be checked for leaks.

The calibration test must be carried out the day before the pumping test to allow the water levels to recover before the actual pump test operations begin.

A maximum stabilised dynamic water level (resulting in the maximum admissible draw-down smax of the borehole) is defined prior to the test as target. It is defined either by:

- The depth of the first screened section (in case the pump is installed below the screens); and

- Two meters above the pump position.

The maximum admissible draw-down smax is sought by trial and error during the equipment test, by slowly increasing the discharge rate and recording the water levels, resulting in the highest possible pumping rate Qmax.

Cases for which the calibration test has to be repeated at the expense of the CONTRACTOR are as follows:

- If the maximum admissible draw-down smax is ‘over-shot’ with the maximum flow rate of the pump during the calibration test, then the pump is oversized and a new test has to be carried out with a smaller pump.

- If the pump is not be capable of producing the required maximum admissible draw-down smax, then two options should be considered:

- Restart the calibration test with a more powerful pump; or

- If the maximum flow rate of the calibration test exceeds the design yield by 150%, the ENGINEER can approve the use of the maximum pump rate for the further tests.

Design of discharge rates for step draw-down pumping test is as follows:

- The maximum discharge rate (Qmax) obtained from the calibration test  is used to design the pumping rates for the step draw-down test, by dividing Qmax by the number of steps and homogeneously distributing the discharge rates over the whole range; and

- During the calibration test, the gate valve shall be graduated and positions of the different discharge rates marked in preparation for the step draw down test.

#### STEP DRAW-DOWN TEST

The continuous step draw-down test shall ideally have six (6) steps, but a minimum of four (4), all the of same time duration, between sixty (60) to one hundred and twenty (120) minutes until water levels stabilise, without intermittent rest period. The test shall begin with the lowest discharge rate and increased consecutively until the maximum discharge rate is reached. Upon completion of the step draw-down test, the recovery shall be monitored for at least two (2) hours or until ninety-five percent (95%) of its pre-pumping level.

#### CONSTANT RATE PUMPING TEST

At the end of the step-draw-down test, the CONTRACTOR carries out a rapid interpretation of the field data to define the borehole constants and calculate the critical yield of the borehole, corresponding to a borehole-efficiency of fifty percent (50%).

The constant rate pumping rate is either defined by the critical yield. If one hundred and twenty percent (120%) of the design yield is lower than the critical yield, the CONTRACTOR can suggest carrying out the constant rate pumping test with this yield.

The ENGINEER must approve the pumping rate to be used for the constant rate pumping test, as obtained from Section 5.2.2.

Constant rate pumping tests will be carried out up to 72 hours but at least 48 hours in length followed by up to a twelve (12) hours recovery period or reaching 95% of the initial static water level (pre-pumping measured water level).

The pump test shall be terminated only after approval by the ENGINEER.

The test pump cannot be removed from the borehole during the recovery periods.

### SANITARY SEAL

Once the surface casing is in place, the annular space between the XX-inch drilled hole and wall of the surface casing shall be grouted for sanitary seal with cement slurry (Section 4.10.3) by a pour-in method from the top for a minimum of 1m below the borehole head.

### HEAD AND CAPPING

The head design is detailed in the drawings which are to be found in APPENDIX 1. The CONTRACTOR shall supply all materials and carry out the construction of the head according to the design drawings provided. The head shall be marked with the borehole number, in a manner approved by the ENGINEER; once pumping tests are completed, an external lockable steel cap shall be provided and fitted as shown in the drawings, allowing for permanent installation of a 1’ dip tube for water level monitoring. Care shall be taken to ensure that the cap is closely fitted and fully seated on the top of the casing, yet easily removable. The locking blade shall be fitted so that it can be easily inserted and removed.

### CLEAN-UP AND CONTAMINATION PREVENTION

The CONTRACTOR shall at all times take every precaution to ensure that the borehole is kept free of contamination.

5.6 DISPOSAL OF WATER

The disposal of water during development and testing is the Contractor's responsibility. The Employer assures that all approvals are in place for safe disposal of water. The Contactor is responsible for all liability, expenses and costs for any damages, losses or claims which might arise from the disposal of water, including without limitation due to flooding, loss of crops, contamination.

## MONITORING, SAMPLING AND LOGGING REQUIREMENTS

### DRILLING FLUID MONITORING

During drilling, readings of the mud condition (pH, viscosity, density and sand content) will be collected and recorded as directed by the ENGINEER. Steps will be taken immediately to correct any variations of the preferred values. Where applicable and required, mud dispersing agents and other chemicals applicable to standard procedures may be used if in accordance with the legal regulations.

### BOREHOLE LOGGING

Penetration rates, measured as minutes per meter drilled, must be recorded for every meter in the drillers log in regard with the pressure on the tool. The CONTRACTOR must report immediately to the ENGINEER on site any changes in the penetration rate. The penetration rate report must include the method of drilling used and if any changes in the drilling method have been undertaken its depth and time of change must be recorded. Drilling interruption for flushing without drilling, stoppage during installation of additional drill pipes, breakdowns, etc. must be properly recorded so that the drilling rates can be properly interpreted purely based on time taken for drilling.

The CONTRACTOR shall endeavour to operate in such a way as to detect water strikes by noting increases in flow rates. The CONTRACTOR submits the method with which increased flow rates are measured for approval to the ENGINEER.

### 6.3	FORMATION SAMPLING

Representative samples of the strata penetrated will be collected every meter (or as otherwise directed and approved by the Engineer), by whatever method is standard for the drilling technique in use.

When requested by the ENGINEER, the samples will be displayed in a neat and organised manner so that the entire geologic section is clearly represented.

### PUMP TEST MONITORING

Results of all pump tests will be provided to the ENGINEER in raw format on sheets detailed as per APPENDIX 2, and in digital format. Full results and preliminary interpretation of the Step Pumping Test with suggested yield for constant rate pump test will be given to the ENGINEER on the day that the step test is completed. The ENGINEER has to approve the constant rate test yield. In the tested borehole, the measurement will be done through a temporary measurement dip tube which shall be deep enough to reach the top of the pump.

#### 6.4.1	WATER LEVEL MONITORING

The water level measurements must be done in the borehole, which is tested and if possible, in up to 2 neighbouring boreholes designated by the ENGINEER.

For the tested borehole, the following indicative time intervals are recommended, as shown in Appendix 2:

Every 1 minute from 0 to 10 minutes of pumping;

Every 2 minutes from 10 to 30 minutes of pumping;

Every 5 minutes from 30 to 60 minutes of pumping;

Every 10 minutes from 60 to 360 minutes of pumping;

Every 15 minutes from 360 to 600 minutes of pumping;

Every 30 minutes from 10 to 24 hours of pumping; and

Every 60 minutes from 24 hours of pumping.

It is crucial that the exact time of a measurement be recorded, even in the event that the above indicative times could not be exactly met.

#### 6.4.2	FLOW RATE MONITORING

The pumping rate from the new production boreholes shall be recorded at fifteen (15) minute intervals specified below within an accuracy of +/- 10% by means of a flow meter or a volumetric gauging device (weir tank) or graduated bucket for low flowing boreholes. The flow meter must be installed such that a full pipe flow exists at all times during pumping and be located in a straight pipe at the borehole site with at least ten (10) pipe diameters length on either side of the meter.

#### 6.4.3	WATER QUALITY MONITORING AND WATER SAMPLING

During pumping operations, temperature, electrical conductivity and pH of pumped water will be recorded for any flow measurement. Water samples for water quality analysis for commissioning of the borehole must be collected during the pumping test as directed by the ENGINEER and in accordance with the legal regulations.

## REPORTING REQUIREMENTS

The Contractor shall submit to the Engineer on a daily basis a progress report describing all activities and all ongoing test results. At the end of the works, a full report including the borehole completion report, the photographic documentation containing a detailed description of the following is submitted to the Engineer and Employer:

- Progress narrative of excavation, pipe laying, concrete placement, backfilling (compilation of all daily activity reports)

- Detailed lithological description with photo documentation of samples;

- Details of casings and installed materials;

- Documentation from pumping tests including all details for the step draw-down and constant rate tests;

- Results of water quality analysis;

- Particulars of other materials, accessories and related materials delivered to the site and those available; in the stores at the end of the works;

- An as-built drawing of the finalised borehole, including the encountered lithological units; and

- All raw data of the calibration, pumping tests including interpretation of pump tests.

The minimum data requirements are all the information listed in quality control checklist in APPENDIX 3.

## APPENDIX 1: TECHNICAL DRAWINGS: BOREHOLE DESIGN, HEAD AND CAPPING

Example technical designs are available upon request- contact UNHCR WASH team in Geneva.

Most often the contractor will submit a proposed design as part of the tender, which will then be used as the basis for discussions and should be agreed and finalised and placed here.  Please contact UNHCR WASH team in Geneva for support.

## APPENDIX 2: STANDARD PUMP TEST FORM

## APPENDIX 3: STANDARD BOREHOLE LOG AND QUALITY CONTROL CHECK LIST

This checklist should be used to ensure that all the appropriate information is collected and documented during all phases of borehole construction including siting, drilling, pump testing, development and completion.

A dummy consists of an axially suspended cylinder (or cage-ring) of at least 7 m length with a minimum external diameter corresponding to the expected pump diameter. The dummy should freely be passed down the borehole without force