Annex A – Specification to RFQ 2021-100

FOR CONTRACT ESTABLISHMENT ON PROVISION OF MAINTENENCE SERVICES OF DIESEL GENERATORS APD33A and APD25 INSTALLED IN UNHCR FIELD OFFICES IN SLOVIANSK, SEVERODONETSK AND MARIUPOL

A- Specification of Services

Quotations should comply with the service specifications set out below.

1. Maintenance period: once a year

2. Emergency call response time: 48 hours

Diesel generators APD33A and APD25A made by AKSA

|  | Weekly maintenance (conducted by UNHCR) |
| --- | --- |
|  | Coolant level control in the engine radiator |
|  | Monitoring the water level in the fuel pre-filter |
|  | Oil level control in the crankcase |
|  | Oil pressure control on pressure gauge on the automatic control panel |
|  | Air filter clogging check on the indicator |
|  | Output parameters values monitoring of the diesel generator during operation under load |
|  | Output parameters values monitoring of the diesel generator in the absence of network outages without load |
|  | Checking the absence of cooling systems leaks, lubrication, fuel supply |
|  | External examination and elimination of contamination (dust, dirt) on the louvres of the supply ventilation and in the protective case |
|  | Checking and topping up distilled water in the battery |
| № | List of work required |
|  | - Annual maintenance (basic) |
|  | ENGINE |
| 1 | Check of the quantity and measure of the density of the coolant. Topping up if necessary. Change the coolant according to the schedule. |
| 2 | Check of the condition and adjustment of the drive belt tension. Replacement according to schedule. |
| 3 | Check of the water presence in the fuel pre-filter and draining water. Change the filter if necessary. |
| 4 | Check of the oil level in the engine crankcase. Check of the oil pressure using a standard pressure gauge. Topping up if necessary. Change of the oil and oil filter according to the manufacturer's recommended schedule. |
| 5 | Cleaning of the air filter and removing dirt from the dust container under normal operating conditions. Change of the filter if necessary. |
| 6 | Battery test, electrolyte level and density control. Top up with distilled water if necessary. Cleaning of the battery. |
| 7 | Monitoring of the condition of the air filter clogging sensor |
| 8 | Checking the operation of sensors and blocking |
| 9 | Cleaning and adjusting the speed sensors |
| 10 | Checking and tightening the mechanical connection of the engine and generator |
| 11 | Check of the condition of the mechanical governor |
| 12 | Test of the diesel generator ability to maintain frequency stably with changing load |
|  | GENERATOR |
| 13 | Open of the diesel generator case, check of the condition of the protective paintwork and lock of marks on the AVR unit |
| 14 | Insulation monitoring and absence of short circuit in generator windings and control systems |
| 15 | Check of the generator power circuits |
| 16 | Check of the control circuits of the generator |
| 17 | Check of the magnetic charged stator status |
| 18 | Check of the main automatic pressure regulator |
| 19 | Check and adjustment of the output pressure |
| 20 | Check and adjustment of DROOP - generator characteristics |
| 21 | Diesel generator testing without load connection |
| 22 | diesel generator testing after connecting the load |
| 23 | Modeling of possible deviations (malfunctions) of the consumer's power supply and checking the functioning of the diesel generator in all modes |
| 24 | Check of the "emergency stop" system operation to launch block from the ATI panel |
| 25 | Control of the processing of the start interval of the diesel generator with the disappearance of the electric voltage up to 10 sec and connect the load up to 15 sec. Working out the intervals for the time of stopping the diesel generator with the restoration of electricity in 5 minutes and switching the load up to 3 minutes |
| 26 | Check of the battery charger operation |
| 27 | Checking of the measuring devices functioning on the diesel generator control panel |
| 28 | Testing the ability of the diesel generator to stably maintain voltage when the load changes |
| 29 | Checking the stability frequency of the generated energy |
|  | AUTOMATION PANEL |
| 30 | Check of the control circuits |
| 31 | Check and set of the current transformation ratio of the control phase |
| 32 | Check and adjustment of the voltage transformation ratio of the control phase |
| 33 | Response time checking and setting |
| 34 | System management and emergency response |
| 35 | Control and adjustment of the input signal from the speed controller |
|  | 2. Additional Services requested |
| 36 | Examination of the generator for defects |
| 37 | Emergency call (if different from item 36) |

Requested materials

| № | List of materials required to four diesel generators service | EOM | Q-ty |
| --- | --- | --- | --- |
| 1 | Statoil Powerway 15W-40 grease | l | 40 |
| 2 | Distilled water | l | 24 |
| 3 | Antifreeze | l | 24 |
| 4 | Fuel filter | pcs | 4 |
| 5 | Oil filter | pcs | 4 |
| 6 | Air filter | pcs | 4 |

Quantities of Diesel Generators APD33A and APD25A manufactured by AKSA in UNHCR offices

| Type of doesel generator | Location | Frequency of technical examination per year |
| --- | --- | --- |
| AKSA APD33A | Mariupol | 1 |
| AKSA APD33A | Sloviansk | 1 |
| AKSA APD25A | Sloviansk | 1 |
| AKSA APD25A | Sievierodonetsk | 1 |

The bidder has to provide with a description of each service it offers. The quotation has to stipulate separately the cost of:

- Annual maintenance (basic),

- additional services (examination of the generator for defects and emergency call),

- materials both for each unit and for 4 diesel generators in general.